## ch.11
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Dielectric Breakdown | Dielectric breakdown |  | NFPA 70B® Enhanced Fluid Sample Analysis Form | Oil-Filled Transformer | OFTR | 70B-ENHANCED | fluidSampleAnalysis
Acid Neutralization Number | Acid neutralization number
Specific Gravity | Specific gravity
Interfacial Tension | Interfacial tension
Color | Color
Visual Condition | Visual condition
Water Content | Water content
Power Factor | Power factor
Dissolved Gas Analysis | Dissolved gas analysis
Furan Analysis | Furan analysis
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Dielectric Breakdown | Dielectric breakdown |  | NFPA 70B® Standard Fluid Sample Analysis Form | Oil-Filled Transformer | OFTR | 70B-STANDARD | fluidSampleAnalysis
Acid Neutralization Number | Acid neutralization number
Specific Gravity | Specific gravity
Interfacial Tension | Interfacial tension
Color | Color
Visual Condition | Visual condition
Water Content | Water content
Power Factor | Power factor
Dissolved Gas Analysis | Dissolved gas analysis
Furan Analysis | Furan analysis
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Dielectric Breakdown | Dielectric breakdown |  | Basic Transformer Fluid Sample Analysis Form | Oil-Filled Transformer | OFTR | BASIC-XFMR | fluidSampleAnalysis
Acid Neutralization Number | Acid neutralization number
Specific Gravity | Specific gravity
Interfacial Tension | Interfacial tension
Color | Color
Visual Condition | Visual condition
Water Content | Water content
Power Factor | Power factor
Dissolved Gas Analysis | Dissolved gas analysis
Furan Analysis | Furan analysis
| testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Bolted connections |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Dry-Type Transformer (<= 600V) | DTTR-LV | 70B-ENHANCED | fluidSampleAnalysis
Cooling devices | Cooling devices
Neutral grounding impedance devices | Neutral grounding impedance devices
Transformer enclosure | Transformer enclosure | Ensure ventilation and equipment enclosure integrity has not been compromised.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Bolted connections |  | NFPA 70B® Enhanced De-Energized Visual Insepction Form | Dry-Type Transformer (> 600V) | DTTR-MV | 70B-ENHANCED | visualInspection
Cooling devices | Cooling devices
Liquid level gauge(s) and alarm(s) | Liquid level gauge(s) and alarm(s)
Neutral grounding impedance devices | Neutral grounding impedance devices
Nitrogen bottle pressure system | Nitrogen bottle pressure system
Pressure relief device(s) | Pressure relief device(s)
Sudden pressure relay(s) | Sudden pressure relay(s)
Tank over/under pressure gauge and alarms | Tank over/under pressure gauge and alarms
Transformer enclosure | Transformer enclosure | Ensure ventilation and equipment enclosure integrity has not been compromised.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Bolted connections |  | NFPA 70B® Enhanced De-Energized Visual Insepction Form | Oil-Filled Transformer | OFTR | 70B-ENHANCED | visualInspection
Cooling devices | Cooling devices
Liquid level gauge(s) and alarm(s) | Liquid level gauge(s) and alarm(s)
Neutral grounding impedance devices | Neutral grounding impedance devices
Nitrogen bottle pressure system | Nitrogen bottle pressure system
Pressure relief device(s) | Pressure relief device(s)
Sudden pressure relay(s) | Sudden pressure relay(s)
Tank over/under pressure gauge and alarms | Tank over/under pressure gauge and alarms
Transformer enclosure | Transformer enclosure | Ensure ventilation and equipment enclosure integrity has not been compromised.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Bolted connections |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Dry-Type Transformer (<= 600V) | DTTR-LV | 70B-STANDARD | visualInspection
Cooling devices | Cooling devices
Neutral grounding impedance devices | Neutral grounding impedance devices
Transformer enclosure | Transformer enclosure | Ensure ventilation and equipment enclosure integrity has not been compromised.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Bolted connections |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Dry-Type Transformer (> 600V) | DTTR-MV | 70B-STANDARD | visualInspection
Cooling devices | Cooling devices
Liquid level gauge(s) and alarm(s) | Liquid level gauge(s) and alarm(s)
Neutral grounding impedance devices | Neutral grounding impedance devices
Nitrogen bottle pressure system | Nitrogen bottle pressure system
Pressure relief device(s) | Pressure relief device(s)
Sudden pressure relay(s) | Sudden pressure relay(s)
Tank over/under pressure gauge and alarms | Tank over/under pressure gauge and alarms
Transformer enclosure | Transformer enclosure | Ensure ventilation and equipment enclosure integrity has not been compromised.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Bolted connections |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Oil-Filled Transformer | OFTR | 70B-STANDARD | visualInspection
Cooling devices | Cooling devices
Liquid level gauge(s) and alarm(s) | Liquid level gauge(s) and alarm(s)
Neutral grounding impedance devices | Neutral grounding impedance devices
Nitrogen bottle pressure system | Nitrogen bottle pressure system
Pressure relief device(s) | Pressure relief device(s)
Sudden pressure relay(s) | Sudden pressure relay(s)
Tank over/under pressure gauge and alarms | Tank over/under pressure gauge and alarms
Transformer enclosure | Transformer enclosure | Ensure ventilation and equipment enclosure integrity has not been compromised.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Transformer enclosure | Transformer enclosure | Ensure ventilation and equipment enclosure integrity has not been compromised. | Basic Energized Visual Inspection Form | Dry-Type Transformer (<= 600V) | DTTR-LV | BASIC | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Transformer enclosure | Transformer enclosure | Ensure ventilation and equipment enclosure integrity has not been compromised. | Basic Energized Visual Inspection Form | Dry-Type Transformer (> 600V) | DTTR-MV | BASIC | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Transformer enclosure | Transformer enclosure | Ensure ventilation and equipment enclosure integrity has not been compromised. | Basic Energized Visual Inspection Form | Oil-Filled Transformer | OFTR | BASIC | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Transformers shall be cleaned to remove buildup of accumulated dirt and debris. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Dry-Type Transformer (<= 600V) | DTTR-LV | 70B-ENHANCED | cleaning
Cleanliness | Transformer bushings and any accessible insulators and conductors shall be wiped clean to remove surface buildup of contaminants.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Transformers shall be cleaned to remove buildup of accumulated dirt and debris. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Dry-Type Transformer (> 600V) | DTTR-MV | 70B-ENHANCED | cleaning
Cleanliness | Transformer bushings and any accessible insulators and conductors shall be wiped clean to remove surface buildup of contaminants.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Transformers shall be cleaned to remove buildup of accumulated dirt and debris. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Oil-Filled Transformer | OFTR | 70B-ENHANCED | cleaning
Cleanliness | Transformer bushings and any accessible insulators and conductors shall be wiped clean to remove surface buildup of contaminants.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Transformers shall be cleaned to remove buildup of accumulated dirt and debris. |  | NFPA 70B® Standard De-Energized Cleaning Form | Dry-Type Transformer (<= 600V) | DTTR-LV | 70B-STANDARD | cleaning
Cleanliness | Transformer bushings and any accessible insulators and conductors shall be wiped clean to remove surface buildup of contaminants.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Transformers shall be cleaned to remove buildup of accumulated dirt and debris. |  | NFPA 70B® Standard De-Energized Cleaning Form | Dry-Type Transformer (> 600V) | DTTR-MV | 70B-STANDARD | cleaning
Cleanliness | Transformer bushings and any accessible insulators and conductors shall be wiped clean to remove surface buildup of contaminants.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Transformers shall be cleaned to remove buildup of accumulated dirt and debris. |  | NFPA 70B® Standard De-Energized Cleaning Form | Oil-Filled Transformer | OFTR | 70B-STANDARD | cleaning
Cleanliness | Transformer bushings and any accessible insulators and conductors shall be wiped clean to remove surface buildup of contaminants.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Verify tightness of accessible bolted electrical connections |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Dry-Type Transformer (<= 600V) | DTTR-LV | 70B-ENHANCED | mechanicalServicing
Tap connections | Verify as-left tap connections are as specified
Anchorage & grounding | Inspect anchorage, alignment, and grounding
Cooling devices | Mechanially service cooling devices
Transformer enclosure | Transformer enclosures, ventilation filters, and screens inspected and replaced or cleaned, as needed
Control cabinets | Control cabinets connections and cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Verify tightness of accessible bolted electrical connections |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Dry-Type Transformer (> 600V) | DTTR-MV | 70B-ENHANCED | mechanicalServicing
Tap connections | Verify as-left tap connections are as specified
Anchorage & grounding | Inspect anchorage, alignment, and grounding
Cooling devices | Mechanially service cooling devices
Transformer enclosure | Transformer enclosures, ventilation filters, and screens inspected and replaced or cleaned, as needed
Control cabinets | Control cabinets connections and cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Verify tightness of accessible bolted electrical connections |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Oil-Filled Transformer | OFTR | 70B-ENHANCED | mechanicalServicing
Tap connections | Verify as-left tap connections are as specified
Anchorage & grounding | Inspect anchorage, alignment, and grounding
Transformer enclosure | Mechanially service cooling devices
Control cabinets | Control cabinets connections and cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Verify tightness of accessible bolted electrical connections |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Dry-Type Transformer (<= 600V) | DTTR-LV | 70B-STANDARD | mechanicalServicing
Tap connections | Verify as-left tap connections are as specified
Anchorage & grounding | Inspect anchorage, alignment, and grounding
Cooling devices | Mechanially service cooling devices
Transformer enclosure | Transformer enclosures, ventilation filters, and screens inspected and replaced or cleaned, as needed
Control cabinets | Control cabinets connections and cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Verify tightness of accessible bolted electrical connections |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Dry-Type Transformer (> 600V) | DTTR-MV | 70B-STANDARD | mechanicalServicing
Tap connections | Verify as-left tap connections are as specified
Anchorage & grounding | Inspect anchorage, alignment, and grounding
Cooling devices | Mechanially service cooling devices
Transformer enclosure | Transformer enclosures, ventilation filters, and screens inspected and replaced or cleaned, as needed
Control cabinets | Control cabinets connections and cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Verify tightness of accessible bolted electrical connections |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Oil-Filled Transformer | OFTR | 70B-STANDARD | mechanicalServicing
Tap connections | Verify as-left tap connections are as specified
Anchorage & grounding | Inspect anchorage, alignment, and grounding
Cooling devices | Mechanially service cooling devices
Control cabinets | Control cabinets connections and cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Insulation resistance | Main insulation resistance |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Dry-Type Transformer (<= 600V) | DTTR-LV | 70B-ENHANCED | electricalTesting
Turns ratio | Turns ratio on all no-load tap changer (NLTC) taps
Turns ratio | Turns ratio on designated tap
Winding resistance | Winding resistance at designated tap
Bolted connections | Bolted connection resistance
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Insulation resistance | Core insulation resistance |  | NFPA 70B® Enhanced De-Energized* Electrical Testing Form | Dry-Type Transformer (> 600V) | DTTR-MV | 70B-ENHANCED | electricalTesting
Excitation current | Excitation current on each phase
Insulation power factor | Insulation power factor
Insulation power factor | Insulation power factor tip-up
Insulation resistance | Main insulation resistance
Neutral grounding | Neutral grounding impedance devices
Partial discharge | Online partial discharge on MV/HV windings* | *test performed energized
Turns ratio | Turns ratio on all no-load tap changer (NLTC) taps
Turns ratio | Turns ratio on designated tap
Winding resistance | Winding resistance at designated tap
Bolted connections | Bolted connection resistance
Applied voltage | Applied voltage test
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Insulation resistance | Core insulation resistance |  | NFPA 70B® Enhanced De-Energized* Electrical Testing Form | Oil-Filled Transformer | OFTR | 70B-ENHANCED | electricalTesting
Excitation current | Excitation current on each phase
Insulation power factor | Insulation power factor
Insulation resistance | Main insulation resistance
Neutral grounding | Neutral grounding impedance devices
Partial discharge | Online partial discharge on MV/HV windings* | *test performed energized
Insulation power factor | Insulation power factor on each bushing
Sweep frequency response | Sweep frequency response analysis
Turns ratio | Turns ratio on all load tap changer (LTC) taps
Turns ratio | Turns ratio on all no-load tap changer (NLTC) taps
Turns ratio | Turns ratio on designated tap
Winding resistance | Winding resistance at designated tap
Bolted connections | Bolted connection resistance
Sweep frequency response | Sweep frequency response analysis
Insulating blanket | Percent oxygen in insulating blanket
Alarms | Testing of transformer alarms, including temperature, liquid level, nitrogen bottle pressure, tank over/under pressure, sudden pressure
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Insulation resistance | Main insulation resistance |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Dry-Type Transformer (<= 600V) | DTTR-LV | 70B-STANDARD | electricalTesting
Turns ratio | Turns ratio on designated tap
Bolted connections | Bolted connection resistance
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Excitation current | Excitation current on each phase |  | NFPA 70B® Standard De-Energized* Electrical Testing Form | Dry-Type Transformer (> 600V) | DTTR-MV | 70B-STANDARD | electricalTesting
Insulation power factor | Insulation power factor
Insulation resistance | Main insulation resistance
Neutral grounding | Neutral grounding impedance devices
Turns ratio | Turns ratio on designated tap
Bolted connections | Bolted connection resistance
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Exictation current | Excitation current on each phase |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Oil-Filled Transformer | OFTR | 70B-STANDARD | electricalTesting
Insulation power factor | Insulation power factor
Insulation Resistance | Main insulation resistance
Neutral Grounding | Neutral grounding impedance devices
Insulation power factor | Insulation power factor on each bushing
Turns ratio | Turns ratio on designated tap
Winding resistance | Winding resistance at designated tap
Bolted connections | Bolted connection resistance
Alarms | Testing of transformer alarms, including temperature, liquid level, nitrogen bottle pressure, tank over/under pressure, sudden pressure

## ch.12
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Switchgear (<= 1000V) | SWGR-LV | 70B-ENHANCED | visualInspection
Anchorage and grounding | Inspect anchorage and grounding | Document if anchorage is not appropriate in accordance with current seismic requirements so improvements can be considered.
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Sizing | Verify circuit breakers, fuses, protective relays, and other type of overload elements are the right sizes and types and correspond to the drawings and the power system studies | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Communicating devices | For connected communicating addressable devices, verify the device addresses are set in accordance with documentation | Confirm addressing or correct device association where protective devices or the human-machine interface (HMI) are connected to multiple devices via a communication network.
Instrument transformers | Verify instrument transformer ratios are correct as installed
Insulators | Inspect insulators for damage or contaminated surfaces
Air filters | Verify air filters or screens are clean and in place
Ventilation | Check all ventilation openings for obstructions and correct operation of any flap or automatic cover intended to assist in arc resistant ratings
Arc Resistant equipment | Inspect arc resistant equipment to ensure all doors are secured and in place
Switch phase barriers | Verify switch phase barriers are in place and in good condition
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Switchgear (> 1000V) | SWGR-MV | 70B-ENHANCED | visualInspection
Anchorage and grounding | Inspect anchorage and grounding | Document if anchorage is not appropriate in accordance with current seismic requirements so improvements can be considered.
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Sizing | Verify circuit breakers, fuses, protective relays, and other type of overload elements are the right sizes and types and correspond to the drawings and the power system studies | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Communicating devices | For connected communicating addressable devices, verify the device addresses are set in accordance with documentation | Confirm addressing or correct device association where protective devices or the human-machine interface (HMI) are connected to multiple devices via a communication network.
Instrument transformers | Verify instrument transformer ratios are correct as installed
Insulators | Inspect insulators for damage or contaminated surfaces
Air filters | Verify air filters or screens are clean and in place
Ventilation | Check all ventilation openings for obstructions and correct operation of any flap or automatic cover intended to assist in arc resistant ratings
Arc Resistant equipment | Inspect arc resistant equipment to ensure all doors are secured and in place
Switch phase barriers | Verify switch phase barriers are in place and in good condition
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Unitized Substation (USS) (<= 1000V) | USSX-LV | 70B-ENHANCED | visualInspection
Anchorage and grounding | Inspect anchorage and grounding | Document if anchorage is not appropriate in accordance with current seismic requirements so improvements can be considered.
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Sizing | Verify circuit breakers, fuses, protective relays, and other type of overload elements are the right sizes and types and correspond to the drawings and the power system studies | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Communicating devices | For connected communicating addressable devices, verify the device addresses are set in accordance with documentation | Confirm addressing or correct device association where protective devices or the human-machine interface (HMI) are connected to multiple devices via a communication network.
Instrument transformers | Verify instrument transformer ratios are correct as installed
Insulators | Inspect insulators for damage or contaminated surfaces
Air filters | Verify air filters or screens are clean and in place
Ventilation | Check all ventilation openings for obstructions and correct operation of any flap or automatic cover intended to assist in arc resistant ratings
Arc Resistant equipment | Inspect arc resistant equipment to ensure all doors are secured and in place
Switch phase barriers | Verify switch phase barriers are in place and in good condition
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Unitized Substation (USS) (> 1000V) | USSX-MV | 70B-ENHANCED | visualInspection
Anchorage and grounding | Inspect anchorage and grounding | Document if anchorage is not appropriate in accordance with current seismic requirements so improvements can be considered.
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Sizing | Verify circuit breakers, fuses, protective relays, and other type of overload elements are the right sizes and types and correspond to the drawings and the power system studies | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Communicating devices | For connected communicating addressable devices, verify the device addresses are set in accordance with documentation | Confirm addressing or correct device association where protective devices or the human-machine interface (HMI) are connected to multiple devices via a communication network.
Instrument transformers | Verify instrument transformer ratios are correct as installed
Insulators | Inspect insulators for damage or contaminated surfaces
Air filters | Verify air filters or screens are clean and in place
Ventilation | Check all ventilation openings for obstructions and correct operation of any flap or automatic cover intended to assist in arc resistant ratings
Arc Resistant equipment | Inspect arc resistant equipment to ensure all doors are secured and in place
Switch phase barriers | Verify switch phase barriers are in place and in good condition
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | NFPA 70B® Standard De-Energized Visual Inspection Form | Switchgear (<= 1000V) | SWGR-LV | 70B-STANDARD | visualInspection
Anchorage and grounding | Inspect anchorage and grounding | Document if anchorage is not appropriate in accordance with current seismic requirements so improvements can be considered.
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Sizing | Verify circuit breakers, fuses, protective relays, and other type of overload elements are the right sizes and types and correspond to the drawings and the power system studies | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Communicating devices | For connected communicating addressable devices, verify the device addresses are set in accordance with documentation | Confirm addressing or correct device association where protective devices or the human-machine interface (HMI) are connected to multiple devices via a communication network.
Insulators | Inspect insulators for damage or contaminated surfaces
Air filters | Verify air filters or screens are clean and in place
Ventilation | Check all ventilation openings for obstructions and correct operation of any flap or automatic cover intended to assist in arc resistant ratings
Arc Resistant equipment | Inspect arc resistant equipment to ensure all doors are secured and in place
Switch phase barriers | Verify switch phase barriers are in place and in good condition
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | NFPA 70B® Standard De-Energized Visual Inspection Form | Switchgear (> 1000V) | SWGR-MV | 70B-STANDARD | visualInspection
Anchorage and grounding | Inspect anchorage and grounding | Document if anchorage is not appropriate in accordance with current seismic requirements so improvements can be considered.
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Sizing | Verify circuit breakers, fuses, protective relays, and other type of overload elements are the right sizes and types and correspond to the drawings and the power system studies | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Communicating devices | For connected communicating addressable devices, verify the device addresses are set in accordance with documentation | Confirm addressing or correct device association where protective devices or the human-machine interface (HMI) are connected to multiple devices via a communication network.
Instrument transformers | Inspect insulators for damage or contaminated surfaces
Air filters | Verify air filters or screens are clean and in place
Ventilation | Check all ventilation openings for obstructions and correct operation of any flap or automatic cover intended to assist in arc resistant ratings
Arc Resistant equipment | Inspect arc resistant equipment to ensure all doors are secured and in place
Switch phase barriers | Verify switch phase barriers are in place and in good condition
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | NFPA 70B® Standard De-Energized Visual Inspection Form | Unitized Substation (USS) (<= 1000V) | USSX-LV | 70B-STANDARD | visualInspection
Anchorage and grounding | Inspect anchorage and grounding | Document if anchorage is not appropriate in accordance with current seismic requirements so improvements can be considered.
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Sizing | Verify circuit breakers, fuses, protective relays, and other type of overload elements are the right sizes and types and correspond to the drawings and the power system studies | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Communicating devices | For connected communicating addressable devices, verify the device addresses are set in accordance with documentation | Confirm addressing or correct device association where protective devices or the human-machine interface (HMI) are connected to multiple devices via a communication network.
Insulators | Inspect insulators for damage or contaminated surfaces
Air filters | Verify air filters or screens are clean and in place
Ventilation | Check all ventilation openings for obstructions and correct operation of any flap or automatic cover intended to assist in arc resistant ratings
Arc Resistant equipment | Inspect arc resistant equipment to ensure all doors are secured and in place
Switch phase barriers | Verify switch phase barriers are in place and in good condition
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | NFPA 70B® Standard De-Energized Visual Inspection Form | Unitized Substation (USS) (> 1000V) | USSX-MV | 70B-STANDARD | visualInspection
Anchorage and grounding | Inspect anchorage and grounding | Document if anchorage is not appropriate in accordance with current seismic requirements so improvements can be considered.
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Sizing | Verify circuit breakers, fuses, protective relays, and other type of overload elements are the right sizes and types and correspond to the drawings and the power system studies | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Communicating devices | For connected communicating addressable devices, verify the device addresses are set in accordance with documentation | Confirm addressing or correct device association where protective devices or the human-machine interface (HMI) are connected to multiple devices via a communication network.
Insulators | Inspect insulators for damage or contaminated surfaces
Air filters | Verify air filters or screens are clean and in place
Ventilation | Check all ventilation openings for obstructions and correct operation of any flap or automatic cover intended to assist in arc resistant ratings
Arc Resistant equipment | Inspect arc resistant equipment to ensure all doors are secured and in place
Switch phase barriers | Verify switch phase barriers are in place and in good condition
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | Basic Energized Visual Inspection Form | Switchgear (<= 1000V) | SWGR-LV | BASIC | visualInspection
Anchorage and grounding | Inspect anchorage and grounding | Document if anchorage is not appropriate in accordance with current seismic requirements so improvements can be considered.
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Sizing | Verify circuit breakers, fuses, protective relays, and other type of overload elements are the right sizes and types and correspond to the drawings and the power system studies | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Communicating devices | For connected communicating addressable devices, verify the device addresses are set in accordance with documentation | Confirm addressing or correct device association where protective devices or the human-machine interface (HMI) are connected to multiple devices via a communication network.
Air filters | Verify air filters or screens are clean and in place
Arc Resistant equipment | Inspect arc resistant equipment to ensure all doors are secured and in place
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | Basic Energized Visual Inspection Form | Switchgear (> 1000V) | SWGR-MV | BASIC | visualInspection
Anchorage and grounding | Inspect anchorage and grounding | Document if anchorage is not appropriate in accordance with current seismic requirements so improvements can be considered.
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Sizing | Verify circuit breakers, fuses, protective relays, and other type of overload elements are the right sizes and types and correspond to the drawings and the power system studies | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Communicating devices | For connected communicating addressable devices, verify the device addresses are set in accordance with documentation | Confirm addressing or correct device association where protective devices or the human-machine interface (HMI) are connected to multiple devices via a communication network.
Air filters | Verify air filters or screens are clean and in place
Arc Resistant equipment | Inspect arc resistant equipment to ensure all doors are secured and in place
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | Basic Energized Visual Inspection Form | Unitized Substation (USS) (<= 1000V) | USSX-LV | BASIC | visualInspection
Anchorage and grounding | Inspect anchorage and grounding | Document if anchorage is not appropriate in accordance with current seismic requirements so improvements can be considered.
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Sizing | Verify circuit breakers, fuses, protective relays, and other type of overload elements are the right sizes and types and correspond to the drawings and the power system studies | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Communicating devices | For connected communicating addressable devices, verify the device addresses are set in accordance with documentation | Confirm addressing or correct device association where protective devices or the human-machine interface (HMI) are connected to multiple devices via a communication network.
Air filters | Verify air filters or screens are clean and in place
Arc Resistant equipment | Inspect arc resistant equipment to ensure all doors are secured and in place
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | Basic Energized Visual Inspection Form | Unitized Substation (USS) (> 1000V) | USSX-MV | BASIC | visualInspection
Anchorage and grounding | Inspect anchorage and grounding | Document if anchorage is not appropriate in accordance with current seismic requirements so improvements can be considered.
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Sizing | Verify circuit breakers, fuses, protective relays, and other type of overload elements are the right sizes and types and correspond to the drawings and the power system studies | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Communicating devices | For connected communicating addressable devices, verify the device addresses are set in accordance with documentation | Confirm addressing or correct device association where protective devices or the human-machine interface (HMI) are connected to multiple devices via a communication network.
Air filters | Verify air filters or screens are clean and in place
Arc Resistant equipment | Inspect arc resistant equipment to ensure all doors are secured and in place
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, insulating materials, and surrounding areas shall be kept clean to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Switchgear (<= 1000V) | SWGR-LV | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, insulating materials, and surrounding areas shall be kept clean to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Switchgear (> 1000V) | SWGR-MV | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, insulating materials, and surrounding areas shall be kept clean to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Unitized Substation (USS) (<= 1000V) | USSX-LV | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, insulating materials, and surrounding areas shall be kept clean to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Unitized Substation (USS) (> 1000V) | USSX-MV | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, insulating materials, and surrounding areas shall be kept clean to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Standard De-Energized Cleaning Form | Switchgear (<= 1000V) | SWGR-LV | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, insulating materials, and surrounding areas shall be kept clean to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Standard De-Energized Cleaning Form | Switchgear (> 1000V) | SWGR-MV | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, insulating materials, and surrounding areas shall be kept clean to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Standard De-Energized Cleaning Form | Unitized Substation (USS) (<= 1000V) | USSX-LV | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, insulating materials, and surrounding areas shall be kept clean to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Standard De-Energized Cleaning Form | Unitized Substation (USS) (> 1000V) | USSX-MV | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Terminating devices, mechanical parts, or operating parts that open, close, insert, and trip a circuit breaker, switch, or protective device shall be lubricated as required per the manufacturer’s instruction manual. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Switchgear (<= 1000V) | SWGR-LV | 70B-ENHANCED | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Terminating devices, mechanical parts, or operating parts that open, close, insert, and trip a circuit breaker, switch, or protective device shall be lubricated as required per the manufacturer’s instruction manual. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Switchgear (> 1000V) | SWGR-MV | 70B-ENHANCED | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Terminating devices, mechanical parts, or operating parts that open, close, insert, and trip a circuit breaker, switch, or protective device shall be lubricated as required per the manufacturer’s instruction manual. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Unitized Substation (USS) (<= 1000V) | USSX-LV | 70B-ENHANCED | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Terminating devices, mechanical parts, or operating parts that open, close, insert, and trip a circuit breaker, switch, or protective device shall be lubricated as required per the manufacturer’s instruction manual. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Unitized Substation (USS) (> 1000V) | USSX-MV | 70B-ENHANCED | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Terminating devices, mechanical parts, or operating parts that open, close, insert, and trip a circuit breaker, switch, or protective device shall be lubricated as required per the manufacturer’s instruction manual. |  | NFPA 70B® Standard De-Energized Lubrication Form | Switchgear (<= 1000V) | SWGR-LV | 70B-STANDARD | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Terminating devices, mechanical parts, or operating parts that open, close, insert, and trip a circuit breaker, switch, or protective device shall be lubricated as required per the manufacturer’s instruction manual. |  | NFPA 70B® Standard De-Energized Lubrication Form | Switchgear (> 1000V) | SWGR-MV | 70B-STANDARD | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Terminating devices, mechanical parts, or operating parts that open, close, insert, and trip a circuit breaker, switch, or protective device shall be lubricated as required per the manufacturer’s instruction manual. |  | NFPA 70B® Standard De-Energized Lubrication Form | Unitized Substation (USS) (<= 1000V) | USSX-LV | 70B-STANDARD | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Terminating devices, mechanical parts, or operating parts that open, close, insert, and trip a circuit breaker, switch, or protective device shall be lubricated as required per the manufacturer’s instruction manual. |  | NFPA 70B® Standard De-Energized Lubrication Form | Unitized Substation (USS) (> 1000V) | USSX-MV | 70B-STANDARD | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Mechanical operation | Check circuit breakers and switches - mechanical operation | See manufacturer’s instructions. | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Switchgear (<= 1000V) | SWGR-LV | 70B-ENHANCED | mechanicalServicing
Bolted connections | Check bolted connection resistance
Current-carrying lubrication | Verify lubrication on moving current-carrying parts and sliding surfaces | See manufacturer’s instructions.
Sequencing | Verify mechanical interlock systems for correct sequencing | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Sequencing | Verify mechanical systems for correct sequencing, including shutters, racking mechanisms, and similar
Cleanliness | Verify filters or screens are clean and in place | Include filters and screens in the room related to the substation or switchgear.
Fuse holders | Verify fuse holders provide mechanical support and contact integrity
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Mechanical operation | Check circuit breakers and switches - mechanical operation | See manufacturer’s instructions. | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Switchgear (> 1000V) | SWGR-MV | 70B-ENHANCED | mechanicalServicing
Bolted connections | Check bolted connection resistance
Current-carrying lubrication | Verify lubrication on moving current-carrying parts and sliding surfaces | See manufacturer’s instructions.
Sequencing | Verify mechanical interlock systems for correct sequencing | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Sequencing | Verify mechanical systems for correct sequencing, including shutters, racking mechanisms, and similar
Cleanliness | Verify filters or screens are clean and in place | Include filters and screens in the room related to the substation or switchgear.
Fuse holders | Verify fuse holders provide mechanical support and contact integrity
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Mechanical operation | Check circuit breakers and switches - mechanical operation | See manufacturer’s instructions. | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Unitized Substation (USS) (<= 1000V) | USSX-LV | 70B-ENHANCED | mechanicalServicing
Bolted connections | Check bolted connection resistance
Current-carrying lubrication | Verify lubrication on moving current-carrying parts and sliding surfaces | See manufacturer’s instructions.
Sequencing | Verify mechanical interlock systems for correct sequencing | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Sequencing | Verify mechanical systems for correct sequencing, including shutters, racking mechanisms, and similar
Cleanliness | Verify filters or screens are clean and in place | Include filters and screens in the room related to the substation or switchgear.
Fuse holders | Verify fuse holders provide mechanical support and contact integrity
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Mechanical operation | Check circuit breakers and switches - mechanical operation | See manufacturer’s instructions. | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Unitized Substation (USS) (> 1000V) | USSX-MV | 70B-ENHANCED | mechanicalServicing
Bolted connections | Check bolted connection resistance
Current-carrying lubrication | Verify lubrication on moving current-carrying parts and sliding surfaces | See manufacturer’s instructions.
Sequencing | Verify mechanical interlock systems for correct sequencing | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Sequencing | Verify mechanical systems for correct sequencing, including shutters, racking mechanisms, and similar
Cleanliness | Verify filters or screens are clean and in place | Include filters and screens in the room related to the substation or switchgear.
Fuse holders | Verify fuse holders provide mechanical support and contact integrity
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Mechanical operation | Check circuit breakers and switches - mechanical operation | See manufacturer’s instructions. | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Switchgear (<= 1000V) | SWGR-LV | 70B-STANDARD | mechanicalServicing
Bolted connections | Check bolted connection resistance
Current-carrying lubrication | Verify lubrication on moving current-carrying parts and sliding surfaces | See manufacturer’s instructions.
Sequencing | Verify mechanical interlock systems for correct sequencing | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Sequencing | Verify mechanical systems for correct sequencing, including shutters, racking mechanisms, and similar
Cleanliness | Verify filters or screens are clean and in place | Include filters and screens in the room related to the substation or switchgear.
Fuse holders | Verify fuse holders provide mechanical support and contact integrity
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Mechanical operation | Check circuit breakers and switches - mechanical operation | See manufacturer’s instructions. | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Switchgear (> 1000V) | SWGR-MV | 70B-STANDARD | mechanicalServicing
Bolted connections | Check bolted connection resistance
Current-carrying lubrication | Verify lubrication on moving current-carrying parts and sliding surfaces | See manufacturer’s instructions.
Sequencing | Verify mechanical interlock systems for correct sequencing | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Sequencing | Verify mechanical systems for correct sequencing, including shutters, racking mechanisms, and similar
Cleanliness | Verify filters or screens are clean and in place | Include filters and screens in the room related to the substation or switchgear.
Fuse holders | Verify fuse holders provide mechanical support and contact integrity
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Mechanical operation | Check circuit breakers and switches - mechanical operation | See manufacturer’s instructions. | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Unitized Substation (USS) (<= 1000V) | USSX-LV | 70B-STANDARD | mechanicalServicing
Bolted connections | Check bolted connection resistance
Current-carrying lubrication | Verify lubrication on moving current-carrying parts and sliding surfaces | See manufacturer’s instructions.
Sequencing | Verify mechanical interlock systems for correct sequencing | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Sequencing | Verify mechanical systems for correct sequencing, including shutters, racking mechanisms, and similar
Cleanliness | Verify filters or screens are clean and in place | Include filters and screens in the room related to the substation or switchgear.
Fuse holders | Verify fuse holders provide mechanical support and contact integrity
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Mechanical operation | Check circuit breakers and switches - mechanical operation | See manufacturer’s instructions. | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Unitized Substation (USS) (> 1000V) | USSX-MV | 70B-STANDARD | mechanicalServicing
Bolted connections | Check bolted connection resistance
Current-carrying lubrication | Verify lubrication on moving current-carrying parts and sliding surfaces | See manufacturer’s instructions.
Sequencing | Verify mechanical interlock systems for correct sequencing | Verify against plans, drawings, and pertinent records, as well as against evidence of current load levels. Some devices might be able to be checked while panel doors are closed.
Sequencing | Verify mechanical systems for correct sequencing, including shutters, racking mechanisms, and similar
Cleanliness | Verify filters or screens are clean and in place | Include filters and screens in the room related to the substation or switchgear.
Fuse holders | Verify fuse holders provide mechanical support and contact integrity
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Verify filters or screens are clean and in place | Include filters and screens in the room related to the substation or switchgear. | Basic Energized Mechanical Servicing Form | Switchgear (<= 1000V) | SWGR-LV | BASIC | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Verify filters or screens are clean and in place | Include filters and screens in the room related to the substation or switchgear. | Basic Energized Mechanical Servicing Form | Switchgear (> 1000V) | SWGR-MV | BASIC | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Verify filters or screens are clean and in place | Include filters and screens in the room related to the substation or switchgear. | Basic Energized Mechanical Servicing Form | Unitized Substation (USS) (<= 1000V) | USSX-LV | BASIC | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Verify filters or screens are clean and in place | Include filters and screens in the room related to the substation or switchgear. | Basic Energized Mechanical Servicing Form | Unitized Substation (USS) (> 1000V) | USSX-MV | BASIC | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Inspect electrical connections for high resistance |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Switchgear (<= 1000V) | SWGR-LV | 70B-ENHANCED | electricalTesting
Ground resistance | Perform ground resistance test | Perform point-to-point test to determine the resistance between the main grounding system and substation/switchgear frames, system neutral, or derived neutral points. Perform fall-of-potential or alternative test on the grounding electrode system.
Insulation resistance | Measure insulation resistance
Insulation resistance | Measure insulation resistance of control wiring
Protective devices | Test protective devices and systems | For surge protective devices, surge arresters, and arc-energy reduction systems, see the manufacturer’s instructions.
System operation | Perform system operational tests | Include emergency or standby sources of power systems to ensure they are available when needed, automatic throw-overs, paralleling controls, interlock systems, or any other operational or maintenance-related control that might be installed.
Environment controls | Where environment controls are provided, check for correct operating condition | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
Instrument transformers | Test control power transformers, instrument transformers, and metering to ensure correct operation
Communication systems | Verify operation of communications systems
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Inspect electrical connections for high resistance |  | NFPA 70B® Enhanced De-Energized* Electrical Testing Form | Switchgear (> 1000V) | SWGR-MV | 70B-ENHANCED | electricalTesting
Ground resistance | Perform ground resistance test | Perform point-to-point test to determine the resistance between the main grounding system and substation/switchgear frames, system neutral, or derived neutral points. Perform fall-of-potential or alternative test on the grounding electrode system.
Insulation resistance | Measure insulation resistance
Insulation resistance | Measure insulation resistance of control wiring
Protective devices | Test protective devices and systems | For surge protective devices, surge arresters, and arc-energy reduction systems, see the manufacturer’s instructions.
System operation | Perform system operational tests | Include emergency or standby sources of power systems to ensure they are available when needed, automatic throw-overs, paralleling controls, interlock systems, or any other operational or maintenance-related control that might be installed.
Dielectric withstand | Perform dielectric withstand test
Partial discharge | Perform online partial discharge (PD) survey* | *This test is performed energized
Environment controls | Where environment controls are provided, check for correct operating condition | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
Instrument transformers | Test control power transformers, instrument transformers, and metering to ensure correct operation
Communication systems | Verify operation of communications systems
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Inspect electrical connections for high resistance |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Unitized Substation (USS) (<= 1000V) | USSX-LV | 70B-ENHANCED | electricalTesting
Ground resistance | Perform ground resistance test | Perform point-to-point test to determine the resistance between the main grounding system and substation/switchgear frames, system neutral, or derived neutral points. Perform fall-of-potential or alternative test on the grounding electrode system.
Insulation resistance | Measure insulation resistance
Insulation resistance | Measure insulation resistance of control wiring
Protective devices | Test protective devices and systems | For surge protective devices, surge arresters, and arc-energy reduction systems, see the manufacturer’s instructions.
System operation | Perform system operational tests | Include emergency or standby sources of power systems to ensure they are available when needed, automatic throw-overs, paralleling controls, interlock systems, or any other operational or maintenance-related control that might be installed.
Environment controls | Where environment controls are provided, check for correct operating condition | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
Instrument transformers | Test control power transformers, instrument transformers, and metering to ensure correct operation
Communication systems | Verify operation of communications systems
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Inspect electrical connections for high resistance |  | NFPA 70B® Enhanced De-Energized* Electrical Testing Form | Unitized Substation (USS) (> 1000V) | USSX-MV | 70B-ENHANCED | electricalTesting
Ground resistance | Perform ground resistance test | Perform point-to-point test to determine the resistance between the main grounding system and substation/switchgear frames, system neutral, or derived neutral points. Perform fall-of-potential or alternative test on the grounding electrode system.
Insulation resistance | Measure insulation resistance
Insulation resistance | Measure insulation resistance of control wiring
Protective devices | Test protective devices and systems | For surge protective devices, surge arresters, and arc-energy reduction systems, see the manufacturer’s instructions.
System operation | Perform system operational tests | Include emergency or standby sources of power systems to ensure they are available when needed, automatic throw-overs, paralleling controls, interlock systems, or any other operational or maintenance-related control that might be installed.
Dielectric withstand | Perform dielectric withstand test
Partial discharge | Perform online partial discharge (PD) survey* | *This test is performed energized
Environment controls | Where environment controls are provided, check for correct operating condition | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
Instrument transformers | Test control power transformers, instrument transformers, and metering to ensure correct operation
Communication systems | Verify operation of communications systems
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Inspect electrical connections for high resistance |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Switchgear (<= 1000V) | SWGR-LV | 70B-STANDARD | electricalTesting
Ground resistance | Perform ground resistance test | Perform point-to-point test to determine the resistance between the main grounding system and substation/switchgear frames, system neutral, or derived neutral points. Perform fall-of-potential or alternative test on the grounding electrode system.
Insulation resistance | Measure insulation resistance
Protective devices | Test protective devices and systems | For surge protective devices, surge arresters, and arc-energy reduction systems, see the manufacturer’s instructions.
System operation | Perform system operational tests | Include emergency or standby sources of power systems to ensure they are available when needed, automatic throw-overs, paralleling controls, interlock systems, or any other operational or maintenance-related control that might be installed.
Environment controls | Where environment controls are provided, check for correct operating condition | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
Instrument transformers | Test control power transformers, instrument transformers, and metering to ensure correct operation
Communication systems | Verify operation of communications systems
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Inspect electrical connections for high resistance |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Switchgear (> 1000V) | SWGR-MV | 70B-STANDARD | electricalTesting
Ground resistance | Perform ground resistance test | Perform point-to-point test to determine the resistance between the main grounding system and substation/switchgear frames, system neutral, or derived neutral points. Perform fall-of-potential or alternative test on the grounding electrode system.
Insulation resistance | Measure insulation resistance
Protective devices | Test protective devices and systems | For surge protective devices, surge arresters, and arc-energy reduction systems, see the manufacturer’s instructions.
System operation | Perform system operational tests | Include emergency or standby sources of power systems to ensure they are available when needed, automatic throw-overs, paralleling controls, interlock systems, or any other operational or maintenance-related control that might be installed.
Environment controls | Where environment controls are provided, check for correct operating condition | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
Instrument transformers | Test control power transformers, instrument transformers, and metering to ensure correct operation
Communication systems | Verify operation of communications systems
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Inspect electrical connections for high resistance |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Unitized Substation (USS) (<= 1000V) | USSX-LV | 70B-STANDARD | electricalTesting
Ground resistance | Perform ground resistance test | Perform point-to-point test to determine the resistance between the main grounding system and substation/switchgear frames, system neutral, or derived neutral points. Perform fall-of-potential or alternative test on the grounding electrode system.
Insulation resistance | Measure insulation resistance
Protective devices | Test protective devices and systems | For surge protective devices, surge arresters, and arc-energy reduction systems, see the manufacturer’s instructions.
System operation | Perform system operational tests | Include emergency or standby sources of power systems to ensure they are available when needed, automatic throw-overs, paralleling controls, interlock systems, or any other operational or maintenance-related control that might be installed.
Environment controls | Where environment controls are provided, check for correct operating condition | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
Instrument transformers | Test control power transformers, instrument transformers, and metering to ensure correct operation
Communication systems | Verify operation of communications systems
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Inspect electrical connections for high resistance |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Unitized Substation (USS) (> 1000V) | USSX-MV | 70B-STANDARD | electricalTesting
Ground resistance | Perform ground resistance test | Perform point-to-point test to determine the resistance between the main grounding system and substation/switchgear frames, system neutral, or derived neutral points. Perform fall-of-potential or alternative test on the grounding electrode system.
Insulation resistance | Measure insulation resistance
Protective devices | Test protective devices and systems | For surge protective devices, surge arresters, and arc-energy reduction systems, see the manufacturer’s instructions.
System operation | Perform system operational tests | Include emergency or standby sources of power systems to ensure they are available when needed, automatic throw-overs, paralleling controls, interlock systems, or any other operational or maintenance-related control that might be installed.
Environment controls | Where environment controls are provided, check for correct operating condition | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
Instrument transformers | Test control power transformers, instrument transformers, and metering to ensure correct operation
Communication systems | Verify operation of communications systems
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Tools | The availability and condition of required dedicated maintenance or operational tools and other test equipment shall be inspected. If found to be defective, the dedicated maintenance or operational tools or other test equipment shall be taken out of service, replaced, or repaired, according to the manufacturer’s specifications. | Examples of dedicated maintenance or operational tools are rack-out devices, hoisting or handling apparatus, and ground and test devices. | NFPA 70B® Enhanced De-Energized Special Testing Form | Switchgear (<= 1000V) | SWGR-LV | 70B-ENHANCED | specialTesting
Lighting | Area lighting, exit and emergency lighting, room HVAC or ventilation systems, and other auxiliary apparatus shall be checked for proper operation.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Tools | The availability and condition of required dedicated maintenance or operational tools and other test equipment shall be inspected. If found to be defective, the dedicated maintenance or operational tools or other test equipment shall be taken out of service, replaced, or repaired, according to the manufacturer’s specifications. | Examples of dedicated maintenance or operational tools are rack-out devices, hoisting or handling apparatus, and ground and test devices. | NFPA 70B® Enhanced De-Energized Special Testing Form | Switchgear (> 1000V) | SWGR-MV | 70B-ENHANCED | specialTesting
Lighting | Area lighting, exit and emergency lighting, room HVAC or ventilation systems, and other auxiliary apparatus shall be checked for proper operation.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Tools | The availability and condition of required dedicated maintenance or operational tools and other test equipment shall be inspected. If found to be defective, the dedicated maintenance or operational tools or other test equipment shall be taken out of service, replaced, or repaired, according to the manufacturer’s specifications. | Examples of dedicated maintenance or operational tools are rack-out devices, hoisting or handling apparatus, and ground and test devices. | NFPA 70B® Enhanced De-Energized Special Testing Form | Unitized Substation (USS) (<= 1000V) | USSX-LV | 70B-ENHANCED | specialTesting
Lighting | Area lighting, exit and emergency lighting, room HVAC or ventilation systems, and other auxiliary apparatus shall be checked for proper operation.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Tools | The availability and condition of required dedicated maintenance or operational tools and other test equipment shall be inspected. If found to be defective, the dedicated maintenance or operational tools or other test equipment shall be taken out of service, replaced, or repaired, according to the manufacturer’s specifications. | Examples of dedicated maintenance or operational tools are rack-out devices, hoisting or handling apparatus, and ground and test devices. | NFPA 70B® Enhanced De-Energized Special Testing Form | Unitized Substation (USS) (> 1000V) | USSX-MV | 70B-ENHANCED | specialTesting
Lighting | Area lighting, exit and emergency lighting, room HVAC or ventilation systems, and other auxiliary apparatus shall be checked for proper operation.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Tools | The availability and condition of required dedicated maintenance or operational tools and other test equipment shall be inspected. If found to be defective, the dedicated maintenance or operational tools or other test equipment shall be taken out of service, replaced, or repaired, according to the manufacturer’s specifications. | Examples of dedicated maintenance or operational tools are rack-out devices, hoisting or handling apparatus, and ground and test devices. | NFPA 70B® Standard De-Energized Special Testing Form | Switchgear (<= 1000V) | SWGR-LV | 70B-STANDARD | specialTesting
Lighting | Area lighting, exit and emergency lighting, room HVAC or ventilation systems, and other auxiliary apparatus shall be checked for proper operation.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Tools | The availability and condition of required dedicated maintenance or operational tools and other test equipment shall be inspected. If found to be defective, the dedicated maintenance or operational tools or other test equipment shall be taken out of service, replaced, or repaired, according to the manufacturer’s specifications. | Examples of dedicated maintenance or operational tools are rack-out devices, hoisting or handling apparatus, and ground and test devices. | NFPA 70B® Standard De-Energized Special Testing Form | Switchgear (> 1000V) | SWGR-MV | 70B-STANDARD | specialTesting
Lighting | Area lighting, exit and emergency lighting, room HVAC or ventilation systems, and other auxiliary apparatus shall be checked for proper operation.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Tools | The availability and condition of required dedicated maintenance or operational tools and other test equipment shall be inspected. If found to be defective, the dedicated maintenance or operational tools or other test equipment shall be taken out of service, replaced, or repaired, according to the manufacturer’s specifications. | Examples of dedicated maintenance or operational tools are rack-out devices, hoisting or handling apparatus, and ground and test devices. | NFPA 70B® Standard De-Energized Special Testing Form | Unitized Substation (USS) (<= 1000V) | USSX-LV | 70B-STANDARD | specialTesting
Lighting | Area lighting, exit and emergency lighting, room HVAC or ventilation systems, and other auxiliary apparatus shall be checked for proper operation.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Tools | The availability and condition of required dedicated maintenance or operational tools and other test equipment shall be inspected. If found to be defective, the dedicated maintenance or operational tools or other test equipment shall be taken out of service, replaced, or repaired, according to the manufacturer’s specifications. | Examples of dedicated maintenance or operational tools are rack-out devices, hoisting or handling apparatus, and ground and test devices. | NFPA 70B® Standard De-Energized Special Testing Form | Unitized Substation (USS) (> 1000V) | USSX-MV | 70B-STANDARD | specialTesting
Lighting | Area lighting, exit and emergency lighting, room HVAC or ventilation systems, and other auxiliary apparatus shall be checked for proper operation.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Tools | The availability and condition of required dedicated maintenance or operational tools and other test equipment shall be inspected. If found to be defective, the dedicated maintenance or operational tools or other test equipment shall be taken out of service, replaced, or repaired, according to the manufacturer’s specifications. | Examples of dedicated maintenance or operational tools are rack-out devices, hoisting or handling apparatus, and ground and test devices. | Basic Energized Special Testing Form | Switchgear (<= 1000V) | SWGR-LV | BASIC | specialTesting
Lighting | Area lighting, exit and emergency lighting, room HVAC or ventilation systems, and other auxiliary apparatus shall be checked for proper operation.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Tools | The availability and condition of required dedicated maintenance or operational tools and other test equipment shall be inspected. If found to be defective, the dedicated maintenance or operational tools or other test equipment shall be taken out of service, replaced, or repaired, according to the manufacturer’s specifications. | Examples of dedicated maintenance or operational tools are rack-out devices, hoisting or handling apparatus, and ground and test devices. | Basic Energized Special Testing Form | Switchgear (> 1000V) | SWGR-MV | BASIC | specialTesting
Lighting | Area lighting, exit and emergency lighting, room HVAC or ventilation systems, and other auxiliary apparatus shall be checked for proper operation.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Tools | The availability and condition of required dedicated maintenance or operational tools and other test equipment shall be inspected. If found to be defective, the dedicated maintenance or operational tools or other test equipment shall be taken out of service, replaced, or repaired, according to the manufacturer’s specifications. | Examples of dedicated maintenance or operational tools are rack-out devices, hoisting or handling apparatus, and ground and test devices. | Basic Energized Special Testing Form | Unitized Substation (USS) (<= 1000V) | USSX-LV | BASIC | specialTesting
Lighting | Area lighting, exit and emergency lighting, room HVAC or ventilation systems, and other auxiliary apparatus shall be checked for proper operation.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Tools | The availability and condition of required dedicated maintenance or operational tools and other test equipment shall be inspected. If found to be defective, the dedicated maintenance or operational tools or other test equipment shall be taken out of service, replaced, or repaired, according to the manufacturer’s specifications. | Examples of dedicated maintenance or operational tools are rack-out devices, hoisting or handling apparatus, and ground and test devices. | Basic Energized Special Testing Form | Unitized Substation (USS) (> 1000V) | USSX-MV | BASIC | specialTesting
Lighting | Area lighting, exit and emergency lighting, room HVAC or ventilation systems, and other auxiliary apparatus shall be checked for proper operation.

## ch.13
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Distribution Panelboard | DPNL | 70B-ENHANCED | visualInspection
Anchorage and grounding | Inspect anchorage and grounding
Sizing | Verify circuit breakers, fuses, and overload elements are the right sizes and types and correspond to the drawings and power system studies
Communication devices | For connected communicating addressable devices, verify the device addresses are set in accordance with documentation | Confirm addressing or correct device association where protective devices or the human machine interface (HMI) are connected to multiple devices via a communication network.
Instrument transformers | Verify instrument transformer ratios are correct
Insulators | Inspect insulators for damage or contaminated surfaces
Filters | Verify filters are clean and in place
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Phase barriers | Verify phase barriers are in place
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Panelboard | PANL | 70B-ENHANCED | visualInspection
Anchorage and grounding | Inspect anchorage and grounding
Sizing | Verify circuit breakers, fuses, and overload elements are the right sizes and types and correspond to the drawings and power system studies
Communication devices | For connected communicating addressable devices, verify the device addresses are set in accordance with documentation | Confirm addressing or correct device association where protective devices or the human machine interface (HMI) are connected to multiple devices via a communication network.
Instrument transformers | Verify instrument transformer ratios are correct
Insulators | Inspect insulators for damage or contaminated surfaces
Filters | Verify filters are clean and in place
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Phase barriers | Verify phase barriers are in place
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Switchboard | SWBD | 70B-ENHANCED | visualInspection
Anchorage and grounding | Inspect anchorage and grounding
Sizing | Verify circuit breakers, fuses, and overload elements are the right sizes and types and correspond to the drawings and power system studies
Communication devices | For connected communicating addressable devices, verify the device addresses are set in accordance with documentation | Confirm addressing or correct device association where protective devices or the human machine interface (HMI) are connected to multiple devices via a communication network.
Instrument transformers | Verify instrument transformer ratios are correct
Insulators | Inspect insulators for damage or contaminated surfaces
Filters | Verify filters are clean and in place
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Phase barriers | Verify phase barriers are in place
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | NFPA 70B® Standard De-Energized Visual Inspection Form | Distribution Panelboard | DPNL | 70B-STANDARD | visualInspection
Anchorage and grounding | Inspect anchorage and grounding
Sizing | Verify circuit breakers, fuses, and overload elements are the right sizes and types and correspond to the drawings and power system studies
Communication devices | For connected communicating addressable devices, verify the device addresses are set in accordance with documentation | Confirm addressing or correct device association where protective devices or the human machine interface (HMI) are connected to multiple devices via a communication network.
Instrument transformers | Verify instrument transformer ratios are correct
Insulators | Inspect insulators for damage or contaminated surfaces
Filters | Verify filters are clean and in place
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Phase barriers | Verify phase barriers are in place
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | NFPA 70B® Standard De-Energized Visual Inspection Form | Panelboard | PANL | 70B-STANDARD | visualInspection
Anchorage and grounding | Inspect anchorage and grounding
Sizing | Verify circuit breakers, fuses, and overload elements are the right sizes and types and correspond to the drawings and power system studies
Communication devices | For connected communicating addressable devices, verify the device addresses are set in accordance with documentation | Confirm addressing or correct device association where protective devices or the human machine interface (HMI) are connected to multiple devices via a communication network.
Instrument transformers | Verify instrument transformer ratios are correct
Insulators | Inspect insulators for damage or contaminated surfaces
Filters | Verify filters are clean and in place
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Phase barriers | Verify phase barriers are in place
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | NFPA 70B® Standard De-Energized Visual Inspection Form | Switchboard | SWBD | 70B-STANDARD | visualInspection
Anchorage and grounding | Inspect anchorage and grounding
Sizing | Verify circuit breakers, fuses, and overload elements are the right sizes and types and correspond to the drawings and power system studies
Communication devices | For connected communicating addressable devices, verify the device addresses are set in accordance with documentation | Confirm addressing or correct device association where protective devices or the human machine interface (HMI) are connected to multiple devices via a communication network.
Instrument transformers | Verify instrument transformer ratios are correct
Insulators | Inspect insulators for damage or contaminated surfaces
Filters | Verify filters are clean and in place
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Phase barriers | Verify phase barriers are in place
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | Basic Energized Visual Inspection Form | Distribution Panelboard | DPNL | BASIC | visualInspection
Anchorage and grounding | Inspect anchorage and grounding
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | Basic Energized Visual Inspection Form | Panelboard | PANL | BASIC | visualInspection
Anchorage and grounding | Inspect anchorage and grounding
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect external physical condition | This includes condition and integrity of applied labels. | Basic Energized Visual Inspection Form | Switchboard | SWBD | BASIC | visualInspection
Anchorage and grounding | Inspect anchorage and grounding
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Environment controls | Visually inspect environmental controls, where provided | Includes, but is not limited to, fans, heaters, thermostats and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Bus insulation, cable insulation, terminals or terminations, electrical equipment surfaces, enclosures, and insulating materials shall be kept in a clean and contaminant-free state. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Distribution Panelboard | DPNL | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Bus insulation, cable insulation, terminals or terminations, electrical equipment surfaces, enclosures, and insulating materials shall be kept in a clean and contaminant-free state. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Panelboard | PANL | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Bus insulation, cable insulation, terminals or terminations, electrical equipment surfaces, enclosures, and insulating materials shall be kept in a clean and contaminant-free state. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Switchboard | SWBD | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Bus insulation, cable insulation, terminals or terminations, electrical equipment surfaces, enclosures, and insulating materials shall be kept in a clean and contaminant-free state. |  | NFPA 70B® Standard De-Energized Cleaning Form | Distribution Panelboard | DPNL | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Bus insulation, cable insulation, terminals or terminations, electrical equipment surfaces, enclosures, and insulating materials shall be kept in a clean and contaminant-free state. |  | NFPA 70B® Standard De-Energized Cleaning Form | Panelboard | PANL | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Bus insulation, cable insulation, terminals or terminations, electrical equipment surfaces, enclosures, and insulating materials shall be kept in a clean and contaminant-free state. |  | NFPA 70B® Standard De-Energized Cleaning Form | Switchboard | SWBD | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Terminating devices, mechanical parts, and operating parts that exist to open, close, insert, and trip a circuit breaker, switch, or protective device shall be lubricated as required in accordance with the manufacturer’s instructions. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Distribution Panelboard | DPNL | 70B-ENHANCED | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Terminating devices, mechanical parts, and operating parts that exist to open, close, insert, and trip a circuit breaker, switch, or protective device shall be lubricated as required in accordance with the manufacturer’s instructions. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Panelboard | PANL | 70B-ENHANCED | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Terminating devices, mechanical parts, and operating parts that exist to open, close, insert, and trip a circuit breaker, switch, or protective device shall be lubricated as required in accordance with the manufacturer’s instructions. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Switchboard | SWBD | 70B-ENHANCED | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Terminating devices, mechanical parts, and operating parts that exist to open, close, insert, and trip a circuit breaker, switch, or protective device shall be lubricated as required in accordance with the manufacturer’s instructions. |  | NFPA 70B® Standard De-Energized Lubrication Form | Distribution Panelboard | DPNL | 70B-STANDARD | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Terminating devices, mechanical parts, and operating parts that exist to open, close, insert, and trip a circuit breaker, switch, or protective device shall be lubricated as required in accordance with the manufacturer’s instructions. |  | NFPA 70B® Standard De-Energized Lubrication Form | Panelboard | PANL | 70B-STANDARD | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Terminating devices, mechanical parts, and operating parts that exist to open, close, insert, and trip a circuit breaker, switch, or protective device shall be lubricated as required in accordance with the manufacturer’s instructions. |  | NFPA 70B® Standard De-Energized Lubrication Form | Switchboard | SWBD | 70B-STANDARD | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Mechanical condition | Inspect mechanical condition |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Distribution Panelboard | DPNL | 70B-ENHANCED | mechanicalServicing
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Anchorage and grounding | Inspect anchorage and grounding
Mechanical operation | Mechanically operate circuit breakers and switches
Bolted connections | Inspect bolted connection integrity
Current-carrying parts | Verify lubrication on moving current-carrying parts and sliding surfaces | See the manufacturer’s instructions.
Mechanical interlock | Verify mechanical interlock systems for correct sequencing
Indicating devices | Verify mechanical indicating devices are functional
Filters | Verify filters are clean and in place
Fuse holders | Verify fuse holders provide mechanical support and contact integrity
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Mechanical condition | Inspect mechanical condition |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Panelboard | PANL | 70B-ENHANCED | mechanicalServicing
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Anchorage and grounding | Inspect anchorage and grounding
Mechanical operation | Mechanically operate circuit breakers and switches
Bolted connections | Inspect bolted connection integrity
Current-carrying parts | Verify lubrication on moving current-carrying parts and sliding surfaces | See the manufacturer’s instructions.
Mechanical interlock | Verify mechanical interlock systems for correct sequencing
Indicating devices | Verify mechanical indicating devices are functional
Filters | Verify filters are clean and in place
Fuse holders | Verify fuse holders provide mechanical support and contact integrity
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Mechanical condition | Inspect mechanical condition |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Switchboard | SWBD | 70B-ENHANCED | mechanicalServicing
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Anchorage and grounding | Inspect anchorage and grounding
Mechanical operation | Mechanically operate circuit breakers and switches
Bolted connections | Inspect bolted connection integrity
Current-carrying parts | Verify lubrication on moving current-carrying parts and sliding surfaces | See the manufacturer’s instructions.
Mechanical interlock | Verify mechanical interlock systems for correct sequencing
Indicating devices | Verify mechanical indicating devices are functional
Filters | Verify filters are clean and in place
Fuse holders | Verify fuse holders provide mechanical support and contact integrity
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Mechanical condition | Inspect mechanical condition |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Distribution Panelboard | DPNL | 70B-STANDARD | mechanicalServicing
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Anchorage and grounding | Inspect anchorage and grounding
Mechanical operation | Mechanically operate circuit breakers and switches
Bolted connections | Inspect bolted connection integrity
Current-carrying parts | Verify lubrication on moving current-carrying parts and sliding surfaces | See the manufacturer’s instructions.
Mechanical interlock | Verify mechanical interlock systems for correct sequencing
Indicating devices | Verify mechanical indicating devices are functional
Filters | Verify filters are clean and in place
Fuse holders | Verify fuse holders provide mechanical support and contact integrity
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Mechanical condition | Inspect mechanical condition |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Panelboard | PANL | 70B-STANDARD | mechanicalServicing
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Anchorage and grounding | Inspect anchorage and grounding
Mechanical operation | Mechanically operate circuit breakers and switches
Bolted connections | Inspect bolted connection integrity
Current-carrying parts | Verify lubrication on moving current-carrying parts and sliding surfaces | See the manufacturer’s instructions.
Mechanical interlock | Verify mechanical interlock systems for correct sequencing
Indicating devices | Verify mechanical indicating devices are functional
Filters | Verify filters are clean and in place
Fuse holders | Verify fuse holders provide mechanical support and contact integrity
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Mechanical condition | Inspect mechanical condition |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Switchboard | SWBD | 70B-STANDARD | mechanicalServicing
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing
Anchorage and grounding | Inspect anchorage and grounding
Mechanical operation | Mechanically operate circuit breakers and switches
Bolted connections | Inspect bolted connection integrity
Current-carrying parts | Verify lubrication on moving current-carrying parts and sliding surfaces | See the manufacturer’s instructions.
Mechanical interlock | Verify mechanical interlock systems for correct sequencing
Indicating devices | Verify mechanical indicating devices are functional
Filters | Verify filters are clean and in place
Fuse holders | Verify fuse holders provide mechanical support and contact integrity
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing |  | Basic Energized Mechanical Servicing Form | Distribution Panelboard | DPNL | BASIC | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing |  | Basic Energized Mechanical Servicing Form | Panelboard | PANL | BASIC | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Maintenance devices | Ensure maintenance devices and tools are available for equipment servicing |  | Basic Energized Mechanical Servicing Form | Switchboard | SWBD | BASIC | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Hardware connections | Check electrical hardware connections |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Distribution Panelboard | DPNL | 70B-ENHANCED | electricalTesting
Insulation resistance | Measure insulation resistance of the main bus
Insulation resistance | Measure insulation resistance of control wiring
Protective devices | Test protective devices and systems | For surge protective devices, surge arresters, and arc-fault energy reduction systems, see the manufacturer’s instructions.
System operational tests | Perform system operational tests | Includes emergency or standby power systems.
Instrument transformers | Test control power transformers, instrument transformers, and metering to ensure correct operation
Environmental controls | Where environmental controls are provided, check for correct operating condition | Includes, but is not limited to, fans, heaters, thermostats, and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Hardware connections | Check electrical hardware connections |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Panelboard | PANL | 70B-ENHANCED | electricalTesting
Insulation resistance | Measure insulation resistance of the main bus
Insulation resistance | Measure insulation resistance of control wiring
Protective devices | Test protective devices and systems | For surge protective devices, surge arresters, and arc-fault energy reduction systems, see the manufacturer’s instructions.
System operational tests | Perform system operational tests | Includes emergency or standby power systems.
Instrument transformers | Test control power transformers, instrument transformers, and metering to ensure correct operation
Environmental controls | Where environmental controls are provided, check for correct operating condition | Includes, but is not limited to, fans, heaters, thermostats, and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Hardware connections | Check electrical hardware connections |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Switchboard | SWBD | 70B-ENHANCED | electricalTesting
Insulation resistance | Measure insulation resistance of the main bus
Insulation resistance | Measure insulation resistance of control wiring
Protective devices | Test protective devices and systems | For surge protective devices, surge arresters, and arc-fault energy reduction systems, see the manufacturer’s instructions.
System operational tests | Perform system operational tests | Includes emergency or standby power systems.
Instrument transformers | Test control power transformers, instrument transformers, and metering to ensure correct operation
Environmental controls | Where environmental controls are provided, check for correct operating condition | Includes, but is not limited to, fans, heaters, thermostats, and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Hardware connections | Check electrical hardware connections |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Distribution Panelboard | DPNL | 70B-STANDARD | electricalTesting
Insulation resistance | Measure insulation resistance of the main bus
Protective devices | Test protective devices and systems | For surge protective devices, surge arresters, and arc-fault energy reduction systems, see the manufacturer’s instructions.
System operational tests | Perform system operational tests | Includes emergency or standby power systems.
Instrument transformers | Test control power transformers, instrument transformers, and metering to ensure correct operation
Environmental controls | Where environmental controls are provided, check for correct operating condition | Includes, but is not limited to, fans, heaters, thermostats, and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Hardware connections | Check electrical hardware connections |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Panelboard | PANL | 70B-STANDARD | electricalTesting
Insulation resistance | Measure insulation resistance of the main bus
Protective devices | Test protective devices and systems | For surge protective devices, surge arresters, and arc-fault energy reduction systems, see the manufacturer’s instructions.
System operational tests | Perform system operational tests | Includes emergency or standby power systems.
Instrument transformers | Test control power transformers, instrument transformers, and metering to ensure correct operation
Environmental controls | Where environmental controls are provided, check for correct operating condition | Includes, but is not limited to, fans, heaters, thermostats, and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Hardware connections | Check electrical hardware connections |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Switchboard | SWBD | 70B-STANDARD | electricalTesting
Insulation resistance | Measure insulation resistance of the main bus
Protective devices | Test protective devices and systems | For surge protective devices, surge arresters, and arc-fault energy reduction systems, see the manufacturer’s instructions.
System operational tests | Perform system operational tests | Includes emergency or standby power systems.
Instrument transformers | Test control power transformers, instrument transformers, and metering to ensure correct operation
Environmental controls | Where environmental controls are provided, check for correct operating condition | Includes, but is not limited to, fans, heaters, thermostats, and humidity control equipment and settings.

## ch.14
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Visually inspect the physical condition of the busway and associated fittings | Look for evidence of moisture contamination, corrosion, and excessive buildup of dust, dirt, or debris. | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Busway (<= 600V) | BUSW-LV | 70B-ENHANCED | visualInspection
Anchorage | Visually inspect anchorage, hangers, and alignment of busway system | Look for loose connections and twisting or bending of lifted supports.
Electrical joints | Visually inspect all areas near electrical joints, terminations, and connections | Visually check connections to be certain that they are clean and secure and show no signs of overheating or discoloration.
Obstruction | Examine outdoor busway to ensure that weepholes are not obstructed and that the joint shield is installed correctly
Ventilation | Inspect ventilation openings on busway and associated fittings
Seals | Look for signs of deterioration of visible seals and gaskets | Outdoor and drip-resistant busways can contain seals and gaskets.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Visually inspect the physical condition of the busway and associated fittings | Look for evidence of moisture contamination, corrosion, and excessive buildup of dust, dirt, or debris. | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Busway (> 600V) | BUSW-MV | 70B-ENHANCED | visualInspection
Anchorage | Visually inspect anchorage, hangers, and alignment of busway system | Look for loose connections and twisting or bending of lifted supports.
Electrical joints | Visually inspect all areas near electrical joints, terminations, and connections | Visually check connections to be certain that they are clean and secure and show no signs of overheating or discoloration.
Obstruction | Examine outdoor busway to ensure that weepholes are not obstructed and that the joint shield is installed correctly
Ventilation | Inspect ventilation openings on busway and associated fittings
Seals | Look for signs of deterioration of visible seals and gaskets | Outdoor and drip-resistant busways can contain seals and gaskets.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Visually inspect the physical condition of the busway and associated fittings | Look for evidence of moisture contamination, corrosion, and excessive buildup of dust, dirt, or debris. | NFPA 70B® Standard De-Energized Visual Inspection Form | Busway (<= 600V) | BUSW-LV | 70B-STANDARD | visualInspection
Anchorage | Visually inspect anchorage, hangers, and alignment of busway system | Look for loose connections and twisting or bending of lifted supports.
Electrical joints | Visually inspect all areas near electrical joints, terminations, and connections | Visually check connections to be certain that they are clean and secure and show no signs of overheating or discoloration.
Obstruction | Examine outdoor busway to ensure that weepholes are not obstructed and that the joint shield is installed correctly
Ventilation | Inspect ventilation openings on busway and associated fittings
Seals | Look for signs of deterioration of visible seals and gaskets | Outdoor and drip-resistant busways can contain seals and gaskets.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Visually inspect the physical condition of the busway and associated fittings | Look for evidence of moisture contamination, corrosion, and excessive buildup of dust, dirt, or debris. | NFPA 70B® Standard De-Energized Visual Inspection Form | Busway (> 600V) | BUSW-MV | 70B-STANDARD | visualInspection
Anchorage | Visually inspect anchorage, hangers, and alignment of busway system | Look for loose connections and twisting or bending of lifted supports.
Electrical joints | Visually inspect all areas near electrical joints, terminations, and connections | Visually check connections to be certain that they are clean and secure and show no signs of overheating or discoloration.
Obstruction | Examine outdoor busway to ensure that weepholes are not obstructed and that the joint shield is installed correctly
Ventilation | Inspect ventilation openings on busway and associated fittings
Seals | Look for signs of deterioration of visible seals and gaskets | Outdoor and drip-resistant busways can contain seals and gaskets.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Visually inspect the physical condition of the busway and associated fittings | Look for evidence of moisture contamination, corrosion, and excessive buildup of dust, dirt, or debris. | Basic Energized Visual Inspection Form | Busway (<= 600V) | BUSW-LV | BASIC | visualInspection
Anchorage | Visually inspect anchorage, hangers, and alignment of busway system | Look for loose connections and twisting or bending of lifted supports.
Obstruction | Examine outdoor busway to ensure that weepholes are not obstructed and that the joint shield is installed correctly
Ventilation | Inspect ventilation openings on busway and associated fittings
Seals | Look for signs of deterioration of visible seals and gaskets | Outdoor and drip-resistant busways can contain seals and gaskets.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Visually inspect the physical condition of the busway and associated fittings | Look for evidence of moisture contamination, corrosion, and excessive buildup of dust, dirt, or debris. | Basic Energized Visual Inspection Form | Busway (> 600V) | BUSW-MV | BASIC | visualInspection
Anchorage | Visually inspect anchorage, hangers, and alignment of busway system | Look for loose connections and twisting or bending of lifted supports.
Obstruction | Examine outdoor busway to ensure that weepholes are not obstructed and that the joint shield is installed correctly
Ventilation | Inspect ventilation openings on busway and associated fittings
Seals | Look for signs of deterioration of visible seals and gaskets | Outdoor and drip-resistant busways can contain seals and gaskets.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Accumulations of dust, dirt, and debris shall be removed from busways using a brush, vacuum cleaner, or clean, lint-free rags. | Where combustible dust is involved, caution should be exercised to ensure that an ignition hazard is not created. | NFPA 70B® Enhanced De-Energized Cleaning Form | Busway (<= 600V) | BUSW-LV | 70B-ENHANCED | cleaning
Cleanliness | Compressed air shall not be used to remove dust, dirt, or debris from busways or associated fittings. | Hydrocarbon spray propellants and hydrocarbon-based sprays or compounds can cause degradation of certain plastics and elastomers. Contact the busway manufacturer before using these products to clean, dry, or lubricate during installation or maintenance.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Accumulations of dust, dirt, and debris shall be removed from busways using a brush, vacuum cleaner, or clean, lint-free rags. | Where combustible dust is involved, caution should be exercised to ensure that an ignition hazard is not created. | NFPA 70B® Enhanced De-Energized Cleaning Form | Busway (> 600V) | BUSW-MV | 70B-ENHANCED | cleaning
Cleanliness | Compressed air shall not be used to remove dust, dirt, or debris from busways or associated fittings. | Hydrocarbon spray propellants and hydrocarbon-based sprays or compounds can cause degradation of certain plastics and elastomers. Contact the busway manufacturer before using these products to clean, dry, or lubricate during installation or maintenance.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Accumulations of dust, dirt, and debris shall be removed from busways using a brush, vacuum cleaner, or clean, lint-free rags. | Where combustible dust is involved, caution should be exercised to ensure that an ignition hazard is not created. | NFPA 70B® Standard De-Energized Cleaning Form | Busway (<= 600V) | BUSW-LV | 70B-STANDARD | cleaning
Cleanliness | Compressed air shall not be used to remove dust, dirt, or debris from busways or associated fittings. | Hydrocarbon spray propellants and hydrocarbon-based sprays or compounds can cause degradation of certain plastics and elastomers. Contact the busway manufacturer before using these products to clean, dry, or lubricate during installation or maintenance.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Accumulations of dust, dirt, and debris shall be removed from busways using a brush, vacuum cleaner, or clean, lint-free rags. | Where combustible dust is involved, caution should be exercised to ensure that an ignition hazard is not created. | NFPA 70B® Standard De-Energized Cleaning Form | Busway (> 600V) | BUSW-MV | 70B-STANDARD | cleaning
Cleanliness | Compressed air shall not be used to remove dust, dirt, or debris from busways or associated fittings. | Hydrocarbon spray propellants and hydrocarbon-based sprays or compounds can cause degradation of certain plastics and elastomers. Contact the busway manufacturer before using these products to clean, dry, or lubricate during installation or maintenance.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Operating mechanisms and interlocks on plug-in units shall be lubricated in accordance with the manufacturer’s instructions. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Busway (<= 600V) | BUSW-LV | 70B-ENHANCED | lubrication
Lubrication | Where no manufacturer’s instructions are available, non-current-carrying mechanisms and interlocks shall be lubricated with a clean, light grease. | Hydrocarbon spray propellants and hydrocarbon-based sprays or compounds can cause degradation of certain plastics and elastomers. Contact the busway manufacturer before using these products to clean, dry, or lubricate during installation or maintenance.
Lubriaction | Excess lubrication shall be wiped off to avoid accumulation of foreign material.
Lubriaction | Where plug-in units are relocated, electrical plug-in connections on plug-in units shall be lubricated in accordance with the manufacturer’s instructions with a conductive lubricant labeled for use on electrical power connections.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Operating mechanisms and interlocks on plug-in units shall be lubricated in accordance with the manufacturer’s instructions. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Busway (> 600V) | BUSW-MV | 70B-ENHANCED | lubrication
Lubrication | Where no manufacturer’s instructions are available, non-current-carrying mechanisms and interlocks shall be lubricated with a clean, light grease. | Hydrocarbon spray propellants and hydrocarbon-based sprays or compounds can cause degradation of certain plastics and elastomers. Contact the busway manufacturer before using these products to clean, dry, or lubricate during installation or maintenance.
Lubriaction | Excess lubrication shall be wiped off to avoid accumulation of foreign material.
Lubriaction | Where plug-in units are relocated, electrical plug-in connections on plug-in units shall be lubricated in accordance with the manufacturer’s instructions with a conductive lubricant labeled for use on electrical power connections.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Operating mechanisms and interlocks on plug-in units shall be lubricated in accordance with the manufacturer’s instructions. |  | NFPA 70B® Standard De-Energized Lubrication Form | Busway (<= 600V) | BUSW-LV | 70B-STANDARD | lubrication
Lubrication | Where no manufacturer’s instructions are available, non-current-carrying mechanisms and interlocks shall be lubricated with a clean, light grease. | Hydrocarbon spray propellants and hydrocarbon-based sprays or compounds can cause degradation of certain plastics and elastomers. Contact the busway manufacturer before using these products to clean, dry, or lubricate during installation or maintenance.
Lubriaction | Excess lubrication shall be wiped off to avoid accumulation of foreign material.
Lubriaction | Where plug-in units are relocated, electrical plug-in connections on plug-in units shall be lubricated in accordance with the manufacturer’s instructions with a conductive lubricant labeled for use on electrical power connections.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Operating mechanisms and interlocks on plug-in units shall be lubricated in accordance with the manufacturer’s instructions. |  | NFPA 70B® Standard De-Energized Lubrication Form | Busway (> 600V) | BUSW-MV | 70B-STANDARD | lubrication
Lubrication | Where no manufacturer’s instructions are available, non-current-carrying mechanisms and interlocks shall be lubricated with a clean, light grease. | Hydrocarbon spray propellants and hydrocarbon-based sprays or compounds can cause degradation of certain plastics and elastomers. Contact the busway manufacturer before using these products to clean, dry, or lubricate during installation or maintenance.
Lubriaction | Excess lubrication shall be wiped off to avoid accumulation of foreign material.
Lubriaction | Where plug-in units are relocated, electrical plug-in connections on plug-in units shall be lubricated in accordance with the manufacturer’s instructions with a conductive lubricant labeled for use on electrical power connections.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Anchorage | Adjust or repair anchorage or hangers to ensure support of the busway |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Busway (<= 600V) | BUSW-LV | 70B-ENHANCED | mechanicalServicing
Operating mechanisms | Exercise plug-in unit operating mechanisms and external operators to confirm they operate to their full ON and OFF positions
Interlocks | Confirm operation of mechanical interlocks and locking means of plug-in units
Ventilation | Clean ventilation openings and weep holes
Covers | Inspect for loose, open, or missing covers or doors on busways and associated fittings | Inspect all plug-in openings, plug-in units, and joints between busway sections. Some covers are not designed to be removed for inspection.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Anchorage | Adjust or repair anchorage or hangers to ensure support of the busway |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Busway (> 600V) | BUSW-MV | 70B-ENHANCED | mechanicalServicing
Ventilation | Clean ventilation openings and weep holes
Cooling system | Inspect forced-air cooling system | Verify operation of forced-air cooling that could be included in metal enclosed bus systems.
Covers | Inspect for loose, open, or missing covers or doors on busways and associated fittings | Inspect all plug-in openings, plug-in units, and joints between busway sections. Some covers are not designed to be removed for inspection.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Anchorage | Adjust or repair anchorage or hangers to ensure support of the busway |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Busway (<= 600V) | BUSW-LV | 70B-STANDARD | mechanicalServicing
Operating mechanisms | Exercise plug-in unit operating mechanisms and external operators to confirm they operate to their full ON and OFF positions
Interlocks | Confirm operation of mechanical interlocks and locking means of plug-in units
Ventilation | Clean ventilation openings and weep holes
Covers | Inspect for loose, open, or missing covers or doors on busways and associated fittings | Inspect all plug-in openings, plug-in units, and joints between busway sections. Some covers are not designed to be removed for inspection.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Anchorage | Adjust or repair anchorage or hangers to ensure support of the busway |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Busway (> 600V) | BUSW-MV | 70B-STANDARD | mechanicalServicing
Ventilation | Clean ventilation openings and weep holes
Cooling system | Inspect forced-air cooling system | Verify operation of forced-air cooling that could be included in metal enclosed bus systems.
Covers | Inspect for loose, open, or missing covers or doors on busways and associated fittings | Inspect all plug-in openings, plug-in units, and joints between busway sections. Some covers are not designed to be removed for inspection.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bus resistance | Perform bus resistance tests |  | NFPA 70B® Enhanced De-Energized* Electrical Testing Form | Busway (<= 600V) | BUSW-LV | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation resistance tests
Environmental controls | Where environmental controls are provided, check for correct operating condition | Includes, but is not limited to, fans, heaters, thermostats, and humidity control equipment and settings.
Insulation power factor | Perform insulation power-factor or dissipation-factor tests
Partial discharge | Perform online partial-discharge survey* | *this test is completed energized
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bus resistance | Perform bus resistance tests |  | NFPA 70B® Enhanced De-Energized* Electrical Testing Form | Busway (> 600V) | BUSW-MV | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation resistance tests
Dielectric withstand | Perform a dielectric withstand voltage test
Environmental controls | Where environmental controls are provided, check for correct operating condition | Includes, but is not limited to, fans, heaters, thermostats, and humidity control equipment and settings.
Insulation power factor | Perform insulation power-factor or dissipation-factor tests
Partial discharge | Perform online partial-discharge survey* | *this test is completed energized
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bus resistance | Perform bus resistance tests |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Busway (<= 600V) | BUSW-LV | 70B-STANDARD | electricalTesting
Insulation resistance | Perform insulation resistance tests
Environmental controls | Where environmental controls are provided, check for correct operating condition | Includes, but is not limited to, fans, heaters, thermostats, and humidity control equipment and settings.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bus resistance | Perform bus resistance tests |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Busway (> 600V) | BUSW-MV | 70B-STANDARD | electricalTesting
Insulation resistance | Perform insulation resistance tests
Dielectric withstand | Perform a dielectric withstand voltage test
Environmental controls | Where environmental controls are provided, check for correct operating condition | Includes, but is not limited to, fans, heaters, thermostats, and humidity control equipment and settings.

## ch.15
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application. |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Low-Voltage Molded Case Circuit Breaker (<= 250A) | MCCB-S-LV | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and frame for evidence of physical damage, cracks from stresses of operation, or contamination.
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition, including corrosion.
Current-carrying parts | Inspect visible current-carrying parts and control devices if applicable for signs of overheating or deterioration.
Cracks | Check for cracks or lack of visual indication for all associated indicating status devices.
Markings | Check all markings on the circuit breaker are legible.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application. |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Low-Voltage Molded Case Circuit Breaker (> 250A) | MCCB-L-LV | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and frame for evidence of physical damage, cracks from stresses of operation, or contamination.
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition, including corrosion.
Current-carrying parts | Inspect visible current-carrying parts and control devices if applicable for signs of overheating or deterioration.
Cracks | Check for cracks or lack of visual indication for all associated indicating status devices.
Markings | Check all markings on the circuit breaker are legible.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application. |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Low-Voltage Insulated Case Circuit Breaker | ICCB | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and frame for evidence of physical damage, cracks from stresses of operation, or contamination.
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition, including corrosion.
Current-carrying parts | Inspect visible current-carrying parts and control devices if applicable for signs of overheating or deterioration.
Arc chutes | Inspect arc chutes for cracks or excessive erosion if applicable.
Cracks | Check for cracks or lack of visual indication for all associated indicating status devices.
Markings | Check all markings on the circuit breaker are legible.
Operating mechanism | Inspect operating mechanism.
Contacts | Check main contact over travel and arcing contact engagement.
Contacts | Check condition of main and arcing contacts.
Insulating links | Check insulating links/push rods and interphase barriers for cracks and defects.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application. |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Low-Voltage Power Circuit Breaker | LVCB | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and frame for evidence of physical damage, cracks from stresses of operation, or contamination.
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition, including corrosion.
Current-carrying parts | Inspect visible current-carrying parts and control devices if applicable for signs of overheating or deterioration.
Arc chutes | Inspect arc chutes for cracks or excessive erosion if applicable.
Cracks | Check for cracks or lack of visual indication for all associated indicating status devices.
Markings | Check all markings on the circuit breaker are legible.
Operating mechanism | Inspect operating mechanism.
Contacts | Check main contact over travel and arcing contact engagement.
Contacts | Check condition of main and arcing contacts.
Insulating links | Check insulating links/push rods and interphase barriers for cracks and defects.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Medium-Voltage Air Magnetic Circuit Breaker | AMCB | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and frame for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Arc chutes | Inspect each arc chute for cracks or excessive erosion
Interlocks | Inspect ground contact, secondary disconnect, close and trip interlocks, levering latch, mechanism-operated contact (MOC), and truck-operated contact (TOC) switches, and all other interlocks
Markings | Check all markings on the circuit breaker are legible
Bushings | Visually inspect bushings for cracks, chips, loss of porcelain, evidence of corona damage, or other physical damage
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Medium-Voltage Vacuum Circuit Breaker | VCCB | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and frame for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Ground | Inspect ground contact, secondary disconnect, close and trip interlocks, levering latch, mechanism-operated contact (MOC), and truck-operated contact (TOC) switches, and all other interlocks
Markings | Check all markings on the circuit breaker are legible
Contacts | Inspect contact erosion indicator mark on vacuum interrupter moving stem | Some manufacturers have visual inspections to determine contact erosion.
Contacts | Inspect contact | Some manufacturers have visual inspections to determine contact wipe.
Bushings | Visually inspect bushings for cracks, chips, loss of porcelain, evidence of corona damage, or other physical damage
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Medim-Votlage Gas Insulated Circuit Breaker | GICB | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and frame for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Ground | Inspect ground contact, secondary disconnect, close and trip interlocks, levering latch, mechanism-operated contact (MOC), and truck-operated contact (TOC) switches, and all other interlocks
Markings | Check all markings on the circuit breaker are legible
Bushings | Visually inspect bushings for cracks, chips, loss of porcelain, evidence of corona damage, or other physical damage
Gas pressure | Check for low gas pressure
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Medium-Voltage Oil Insulated Circuit Breaker | OICB | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and frame for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Ground | Inspect ground contact, secondary disconnect, close and trip interlocks, levering latch, mechanism-operated contact (MOC), and truck-operated contact (TOC) switches, and all other interlocks
Markings | Check all markings on the circuit breaker are legible
Oil level | Verify correct oil level
Oil leaks | Check for oil leaks
Bushings | Visually inspect bushings for cracks, chips, loss of porcelain, evidence of corona damage, or other physical damage
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application. |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Low-Voltage Molded Case Circuit Breaker (<= 250A) | MCCB-S-LV | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and frame for evidence of physical damage, cracks from stresses of operation, or contamination.
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition, including corrosion.
Current-carrying parts | Inspect visible current-carrying parts and control devices if applicable for signs of overheating or deterioration.
Assosciated indicating devices | Check for cracks or lack of visual indication for all associated indicating status devices.
Markings | Check all markings on the circuit breaker are legible.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application. |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Low-Voltage Molded Case Circuit Breaker (> 250A) | MCCB-L-LV | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and frame for evidence of physical damage, cracks from stresses of operation, or contamination.
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition, including corrosion.
Current-carrying parts | Inspect visible current-carrying parts and control devices if applicable for signs of overheating or deterioration.
Assosciated indicating devices | Check for cracks or lack of visual indication for all associated indicating status devices.
Markings | Check all markings on the circuit breaker are legible.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application. |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Low-Voltage Insulated Case Circuit Breaker | ICCB | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and frame for evidence of physical damage, cracks from stresses of operation, or contamination.
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition, including corrosion.
Current-carrying parts | Inspect visible current-carrying parts and control devices if applicable for signs of overheating or deterioration.
Arc chutes | Inspect arc chutes for cracks or excessive erosion if applicable.
Assosciated indicating devices | Check for cracks or lack of visual indication for all associated indicating status devices.
Markings | Check all markings on the circuit breaker are legible.
Operating mechanism | Inspect operating mechanism.
Contacts | Check main contact over travel and arcing contact engagement.
Contacts | Check condition of main and arcing contacts.
Insulating links | Check insulating links/push rods and interphase barriers for cracks and defects.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application. |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Low-Voltage Power Circuit Breaker | LVCB | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and frame for evidence of physical damage, cracks from stresses of operation, or contamination.
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition, including corrosion.
Current-carrying parts | Inspect visible current-carrying parts and control devices if applicable for signs of overheating or deterioration.
Arc chutes | Inspect arc chutes for cracks or excessive erosion if applicable.
Assosciated indicating devices | Check for cracks or lack of visual indication for all associated indicating status devices.
Markings | Check all markings on the circuit breaker are legible.
Operating mechanism | Inspect operating mechanism.
Contacts | Check main contact over travel and arcing contact engagement.
Contacts | Check condition of main and arcing contacts.
Insulating links | Check insulating links/push rods and interphase barriers for cracks and defects.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Medium-Voltage Air Magnetic Circuit Breaker | AMCB | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and frame for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Arc chutes | Inspect each arc chute for cracks or excessive erosion
Interlocks | Inspect ground contact, secondary disconnect, close and trip interlocks, levering latch, mechanism-operated contact (MOC), and truck-operated contact (TOC) switches, and all other interlocks
Markings | Check all markings on the circuit breaker are legible
Bushings | Visually inspect bushings for cracks, chips, loss of porcelain, evidence of corona damage, or other physical damage
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Medium-Voltage Vacuum Circuit Breaker | VCCB | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and frame for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Arc chutes | Inspect ground contact, secondary disconnect, close and trip interlocks, levering latch, mechanism-operated contact (MOC), and truck-operated contact (TOC) switches, and all other interlocks
Markings | Check all markings on the circuit breaker are legible
Contacts | Inspect contact erosion indicator mark on vacuum interrupter moving stem | Some manufacturers have visual inspections to determine contact erosion.
Contacts | Inspect contact | Some manufacturers have visual inspections to determine contact wipe.
Bushings | Visually inspect bushings for cracks, chips, loss of porcelain, evidence of corona damage, or other physical damage
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Medim-Votlage Gas Insulated Circuit Breaker | GICB | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and frame for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Arc chutes | Inspect ground contact, secondary disconnect, close and trip interlocks, levering latch, mechanism-operated contact (MOC), and truck-operated contact (TOC) switches, and all other interlocks
Markings | Check all markings on the circuit breaker are legible
Bushings | Visually inspect bushings for cracks, chips, loss of porcelain, evidence of corona damage, or other physical damage
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Medium-Voltage Oil Insulated Circuit Breaker | OICB | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and frame for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Arc chutes | Inspect ground contact, secondary disconnect, close and trip interlocks, levering latch, mechanism-operated contact (MOC), and truck-operated contact (TOC) switches, and all other interlocks
Markings | Check all markings on the circuit breaker are legible
Oil level | Verify correct oil level
Oil Leaks | Check for oil leaks
Bushings | Visually inspect bushings for cracks, chips, loss of porcelain, evidence of corona damage, or other physical damage
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application. |  | Basic Energized Visual Inspection Form | Low-Voltage Molded Case Circuit Breaker (<= 250A) | MCCB-S-LV | BASIC | visualInspection
Markings | Check for cracks or lack of visual indication for all associated indicating status devices.
Markings | Check all markings on the circuit breaker are legible.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application. |  | Basic Energized Visual Inspection Form | Low-Voltage Molded Case Circuit Breaker (> 250A) | MCCB-L-LV | BASIC | visualInspection
Markings | Check for cracks or lack of visual indication for all associated indicating status devices.
Markings | Check all markings on the circuit breaker are legible.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application. |  | Basic Energized Visual Inspection Form | Low-Voltage Insulated Case Circuit Breaker | ICCB | BASIC | visualInspection
Markings | Check for cracks or lack of visual indication for all associated indicating status devices.
Markings | Check all markings on the circuit breaker are legible.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application. |  | Basic Energized Visual Inspection Form | Low-Voltage Power Circuit Breaker | LVCB | BASIC | visualInspection
Markings | Check for cracks or lack of visual indication for all associated indicating status devices.
Markings | Check all markings on the circuit breaker are legible.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application |  | Basic Energized Visual Inspection Form | Medium-Voltage Air Magnetic Circuit Breaker | AMCB | BASIC | visualInspection
Markings | Check all markings on the circuit breaker are legible
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application |  | Basic Energized Visual Inspection Form | Medium-Voltage Vacuum Circuit Breaker | VCCB | BASIC | visualInspection
Markings | Check all markings on the circuit breaker are legible
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application |  | Basic Energized Visual Inspection Form | Medim-Votlage Gas Insulated Circuit Breaker | GICB | BASIC | visualInspection
Markings | Check all markings on the circuit breaker are legible
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ratings | Verify ratings for proper system application |  | Basic Energized Visual Inspection Form | Medium-Voltage Oil Insulated Circuit Breaker | OICB | BASIC | visualInspection
Markings | Check all markings on the circuit breaker are legible
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean insulating surfaces of the circuit breaker using a lint-free dry cloth, brush, or vacuum cleaner (avoid blowing material into the circuit breaker or into surrounding equipment) |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Low-Voltage Molded Case Circuit Breaker (<= 250A) | MCCB-S-LV | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean insulating surfaces of the circuit breaker using a lint-free dry cloth, brush, or vacuum cleaner (avoid blowing material into the circuit breaker or into surrounding equipment) |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Low-Voltage Molded Case Circuit Breaker (> 250A) | MCCB-L-LV | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean insulating surfaces of the circuit breaker using a lint-free dry cloth, brush, or vacuum cleaner (avoid blowing material into the circuit breaker or into surrounding equipment) |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Low-Voltage Insulated Case Circuit Breaker | ICCB | 70B-ENHANCED | cleaning
Cleanliness | Clean contact surfaces in accordance with the manufacturer’s instructions
Cleanliness | Clean circuit breaker interior frame
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean insulating surfaces of the circuit breaker using a lint-free dry cloth, brush, or vacuum cleaner (avoid blowing material into the circuit breaker or into surrounding equipment) |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Low-Voltage Power Circuit Breaker | LVCB | 70B-ENHANCED | cleaning
Cleanliness | Clean contact surfaces in accordance with the manufacturer’s instructions
Cleanliness | Clean circuit breaker interior frame
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean insulating surfaces of the circuit breaker using a lint-free dry cloth, brush, or vacuum cleaner (avoid blowing material into the circuit breaker or into surrounding equipment) |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Medium-Voltage Air Magnetic Circuit Breaker | AMCB | 70B-ENHANCED | cleaning
Cleanliness | Clean contact surfaces
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean insulating surfaces of the circuit breaker using a lint-free dry cloth, brush, or vacuum cleaner (avoid blowing material into the circuit breaker or into surrounding equipment) | For vacuum circuit breakers, follow the manufacturer’s instructions to avoid shock due to inherent capacitance from the technology used in the circuit breaker. | NFPA 70B® Enhanced De-Energized Cleaning Form | Medium-Voltage Vacuum Circuit Breaker | VCCB | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean contact surfaces |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Medium-Voltage Oil Insulated Circuit Breaker | OICB | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean insulating surfaces of the circuit breaker using a lint-free dry cloth, brush, or vacuum cleaner (avoid blowing material into the circuit breaker or into surrounding equipment) |  | NFPA 70B® Standard De-Energized Cleaning Form | Low-Voltage Molded Case Circuit Breaker (<= 250A) | MCCB-S-LV | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean insulating surfaces of the circuit breaker using a lint-free dry cloth, brush, or vacuum cleaner (avoid blowing material into the circuit breaker or into surrounding equipment) |  | NFPA 70B® Standard De-Energized Cleaning Form | Low-Voltage Molded Case Circuit Breaker (> 250A) | MCCB-L-LV | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean insulating surfaces of the circuit breaker using a lint-free dry cloth, brush, or vacuum cleaner (avoid blowing material into the circuit breaker or into surrounding equipment) |  | NFPA 70B® Standard De-Energized Cleaning Form | Low-Voltage Insulated Case Circuit Breaker | ICCB | 70B-STANDARD | cleaning
Cleanliness | Clean contact surfaces in accordance with the manufacturer’s instructions
Cleanliness | Clean circuit breaker interior frame
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean insulating surfaces of the circuit breaker using a lint-free dry cloth, brush, or vacuum cleaner (avoid blowing material into the circuit breaker or into surrounding equipment) |  | NFPA 70B® Standard De-Energized Cleaning Form | Low-Voltage Power Circuit Breaker | LVCB | 70B-STANDARD | cleaning
Cleanliness | Clean contact surfaces in accordance with the manufacturer’s instructions
Cleanliness | Clean circuit breaker interior frame
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean insulating surfaces of the circuit breaker using a lint-free dry cloth, brush, or vacuum cleaner (avoid blowing material into the circuit breaker or into surrounding equipment) |  | NFPA 70B® Standard De-Energized Cleaning Form | Medium-Voltage Air Magnetic Circuit Breaker | AMCB | 70B-STANDARD | cleaning
Cleanliness | Clean contact surfaces
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean insulating surfaces of the circuit breaker using a lint-free dry cloth, brush, or vacuum cleaner (avoid blowing material into the circuit breaker or into surrounding equipment) | For vacuum circuit breakers, follow the manufacturer’s instructions to avoid shock due to inherent capacitance from the technology used in the circuit breaker. | NFPA 70B® Standard De-Energized Cleaning Form | Medium-Voltage Vacuum Circuit Breaker | VCCB | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean contact surfaces |  | NFPA 70B® Standard De-Energized Cleaning Form | Medium-Voltage Oil Insulated Circuit Breaker | OICB | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed contacts as specified by the manufacturer |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Low-Voltage Insulated Case Circuit Breaker | ICCB | 70B-ENHANCED | lubrication
Lubriaction | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces as specified by the manufacturer
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed contacts as specified by the manufacturer |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Low-Voltage Power Circuit Breaker | LVCB | 70B-ENHANCED | lubrication
Lubriaction | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces as specified by the manufacturer
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed contacts as specified by the manufacturer |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Medium-Voltage Air Magnetic Circuit Breaker | AMCB | 70B-ENHANCED | lubrication
Lubriaction | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces as specified by the manufacturer
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed contacts as specified by the manufacturer |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Medium-Voltage Vacuum Circuit Breaker | VCCB | 70B-ENHANCED | lubrication
Lubriaction | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces as specified by the manufacturer
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed contacts as specified by the manufacturer |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Medim-Votlage Gas Insulated Circuit Breaker | GICB | 70B-ENHANCED | lubrication
Lubriaction | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces as specified by the manufacturer
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed contacts as specified by the manufacturer |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Medium-Voltage Oil Insulated Circuit Breaker | OICB | 70B-ENHANCED | lubrication
Lubriaction | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces as specified by the manufacturer
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed contacts as specified by the manufacturer |  | NFPA 70B® Standard De-Energized Lubrication Form | Low-Voltage Insulated Case Circuit Breaker | ICCB | 70B-STANDARD | lubrication
Lubriaction | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces as specified by the manufacturer
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed contacts as specified by the manufacturer |  | NFPA 70B® Standard De-Energized Lubrication Form | Low-Voltage Power Circuit Breaker | LVCB | 70B-STANDARD | lubrication
Lubriaction | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces as specified by the manufacturer
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed contacts as specified by the manufacturer |  | NFPA 70B® Standard De-Energized Lubrication Form | Medium-Voltage Air Magnetic Circuit Breaker | AMCB | 70B-STANDARD | lubrication
Lubriaction | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces as specified by the manufacturer
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed contacts as specified by the manufacturer |  | NFPA 70B® Standard De-Energized Lubrication Form | Medium-Voltage Vacuum Circuit Breaker | VCCB | 70B-STANDARD | lubrication
Lubriaction | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces as specified by the manufacturer
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed contacts as specified by the manufacturer |  | NFPA 70B® Standard De-Energized Lubrication Form | Medim-Votlage Gas Insulated Circuit Breaker | GICB | 70B-STANDARD | lubrication
Lubriaction | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces as specified by the manufacturer
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed contacts as specified by the manufacturer |  | NFPA 70B® Standard De-Energized Lubrication Form | Medium-Voltage Oil Insulated Circuit Breaker | OICB | 70B-STANDARD | lubrication
Lubriaction | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces as specified by the manufacturer
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Check all accessible electrical hardware connections for correct torque |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Low-Voltage Molded Case Circuit Breaker (<= 250A) | MCCB-S-LV | 70B-ENHANCED | mechanicalServicing
Operation | Operate the circuit breaker three times
Interlocks | Verify operation and alignment of mechanical safety interlocks, where applicable
Shutter assemblies | Verify correct operation of shutter assemblies on draw-out circuit breakers
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Check all accessible electrical hardware connections for correct torque |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Low-Voltage Molded Case Circuit Breaker (> 250A) | MCCB-L-LV | 70B-ENHANCED | mechanicalServicing
Operation | Operate the circuit breaker three times
Interlocks | Verify operation and alignment of mechanical safety interlocks, where applicable
Shutter assemblies | Verify correct operation of shutter assemblies on draw-out circuit breakers
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Check all accessible electrical hardware connections for correct torque |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Low-Voltage Insulated Case Circuit Breaker | ICCB | 70B-ENHANCED | mechanicalServicing
Operation | Operate the circuit breaker three times
Interlocks | Verify operation and alignment of mechanical safety interlocks, where applicable
Shutter assemblies | Verify correct operation of shutter assemblies on draw-out circuit breakers
Arc chutes | Inspect arc chutes for cracks or excessive erosion if applicable.
Trip bar force | Measure and record trip bar force
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Check all accessible electrical hardware connections for correct torque |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Low-Voltage Power Circuit Breaker | LVCB | 70B-ENHANCED | mechanicalServicing
Operation | Operate the circuit breaker three times
Interlocks | Verify operation and alignment of mechanical safety interlocks, where applicable
Shutter assemblies | Verify correct operation of shutter assemblies on draw-out circuit breakers
Arc chutes | Inspect arc chutes for cracks or excessive erosion if applicable.
Trip bar force | Measure and record trip bar force
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Check all accessible electrical hardware connections for proper torque |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Medium-Voltage Air Magnetic Circuit Breaker | AMCB | 70B-ENHANCED | mechanicalServicing
Barriers | Replace any barriers and parts that have been removed for maintenance
Operation | Close and open the circuit breaker
Interlocks | Verify operation and alignment of mechanical safety interlocks, where applicable
Operation | Verify the proper operation of all circuit breaker/cell accessories, shutters, auxiliary switches, cell MOC and TOC switches, and key interlocks
Operation | Verify proper operation of all cell status indicators
Spring | Charge closing spring and close manually
Trip bar force | Measure and record trip bar force
Fittings | Inspect pneumatic and hydraulic fittings and connections for leaks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Check all accessible electrical hardware connections for proper torque |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Medium-Voltage Vacuum Circuit Breaker | VCCB | 70B-ENHANCED | mechanicalServicing
Barriers | Replace any barriers and parts that have been removed for maintenance
Operation | Close and open the circuit breaker
Interlocks | Verify operation and alignment of mechanical safety interlocks, where applicable
Operation | Verify the proper operation of all circuit breaker/cell accessories, shutters, auxiliary switches, cell MOC and TOC switches, and key interlocks
Operation | Verify proper operation of all cell status indicators
Closing spring | Charge closing spring and close manually
Trip bar force | Measure and record trip bar force
Fittings | Inspect pneumatic and hydraulic fittings and connections for leaks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Check all accessible electrical hardware connections for proper torque |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Medim-Votlage Gas Insulated Circuit Breaker | GICB | 70B-ENHANCED | mechanicalServicing
Barriers | Replace any barriers and parts that have been removed for maintenance
Operation | Close and open the circuit breaker
Interlocks | Verify operation and alignment of mechanical safety interlocks, where applicable
Operation | Verify the proper operation of all circuit breaker/cell accessories, shutters, auxiliary switches, cell MOC and TOC switches, and key interlocks
Operation | Verify proper operation of all cell status indicators
Closing spring | Charge closing spring and close manually
Trip bar force | Measure and record trip bar force
Gas leakage | Perform gas leakage detection
Fittings | Inspect pneumatic and hydraulic fittings and connections for leaks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Check all accessible electrical hardware connections for proper torque |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Medium-Voltage Oil Insulated Circuit Breaker | OICB | 70B-ENHANCED | mechanicalServicing
Barriers | Replace any barriers and parts that have been removed for maintenance
Operation | Close and open the circuit breaker
Interlocks | Verify operation and alignment of mechanical safety interlocks, where applicable
Operation | Verify the proper operation of all circuit breaker/cell accessories, shutters, auxiliary switches, cell MOC and TOC switches, and key interlocks
Operation | Verify proper operation of all cell status indicators
Closing spring | Charge closing spring and close manually
Trip bar force | Measure and record trip bar force
Fittings | Inspect pneumatic and hydraulic fittings and connections for leaks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Check all accessible electrical hardware connections for correct torque |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Low-Voltage Molded Case Circuit Breaker (<= 250A) | MCCB-S-LV | 70B-STANDARD | mechanicalServicing
Operation | Operate the circuit breaker three times
Interlocks | Verify operation and alignment of mechanical safety interlocks, where applicable
Shutter assemblies | Verify correct operation of shutter assemblies on draw-out circuit breakers
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Check all accessible electrical hardware connections for correct torque |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Low-Voltage Molded Case Circuit Breaker (> 250A) | MCCB-L-LV | 70B-STANDARD | mechanicalServicing
Operation | Operate the circuit breaker three times
Interlocks | Verify operation and alignment of mechanical safety interlocks, where applicable
Shutter assemblies | Verify correct operation of shutter assemblies on draw-out circuit breakers
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Check all accessible electrical hardware connections for correct torque |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Low-Voltage Insulated Case Circuit Breaker | ICCB | 70B-STANDARD | mechanicalServicing
Operation | Operate the circuit breaker three times
Interlocks | Verify operation and alignment of mechanical safety interlocks, where applicable
Shutter assemblies | Verify correct operation of shutter assemblies on draw-out circuit breakers
Arc chutes | Inspect arc chutes for cracks or excessive erosion if applicable.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Check all accessible electrical hardware connections for correct torque |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Low-Voltage Power Circuit Breaker | LVCB | 70B-STANDARD | mechanicalServicing
Operation | Operate the circuit breaker three times
Interlocks | Verify operation and alignment of mechanical safety interlocks, where applicable
Shutter assemblies | Verify correct operation of shutter assemblies on draw-out circuit breakers
Arc chutes | Inspect arc chutes for cracks or excessive erosion if applicable.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Check all accessible electrical hardware connections for proper torque |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Medium-Voltage Air Magnetic Circuit Breaker | AMCB | 70B-STANDARD | mechanicalServicing
Barriers | Replace any barriers and parts that have been removed for maintenance
Operation | Close and open the circuit breaker
Operation | Verify operation and alignment of mechanical safety interlocks, where applicable
Operation | Verify the proper operation of all circuit breaker/cell accessories, shutters, auxiliary switches, cell MOC and TOC switches, and key interlocks
Operation | Verify proper operation of all cell status indicators
Spring | Charge closing spring and close manually
Fitting | Inspect pneumatic and hydraulic fittings and connections for leaks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Check all accessible electrical hardware connections for proper torque |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Medium-Voltage Vacuum Circuit Breaker | VCCB | 70B-STANDARD | mechanicalServicing
Barriers | Replace any barriers and parts that have been removed for maintenance
Operation | Close and open the circuit breaker
Operation | Verify operation and alignment of mechanical safety interlocks, where applicable
Operation | Verify the proper operation of all circuit breaker/cell accessories, shutters, auxiliary switches, cell MOC and TOC switches, and key interlocks
Operation | Verify proper operation of all cell status indicators
Spring | Charge closing spring and close manually
Fitting | Inspect pneumatic and hydraulic fittings and connections for leaks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Check all accessible electrical hardware connections for proper torque |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Medim-Votlage Gas Insulated Circuit Breaker | GICB | 70B-STANDARD | mechanicalServicing
Barriers | Replace any barriers and parts that have been removed for maintenance
Operation | Close and open the circuit breaker
Operation | Verify operation and alignment of mechanical safety interlocks, where applicable
Operation | Verify the proper operation of all circuit breaker/cell accessories, shutters, auxiliary switches, cell MOC and TOC switches, and key interlocks
Operation | Verify proper operation of all cell status indicators
Spring | Charge closing spring and close manually
Gas leakage | Perform gas leakage detection
Fitting | Inspect pneumatic and hydraulic fittings and connections for leaks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Electrical connections | Check all accessible electrical hardware connections for proper torque |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Medium-Voltage Oil Insulated Circuit Breaker | OICB | 70B-STANDARD | mechanicalServicing
Barriers | Replace any barriers and parts that have been removed for maintenance
Operation | Close and open the circuit breaker
Operation | Verify operation and alignment of mechanical safety interlocks, where applicable
Operation | Verify the proper operation of all circuit breaker/cell accessories, shutters, auxiliary switches, cell MOC and TOC switches, and key interlocks
Operation | Verify proper operation of all cell status indicators
Spring | Charge closing spring and close manually
Fitting | Inspect pneumatic and hydraulic fittings and connections for leaks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Low-Voltage Molded Case Circuit Breaker (<= 250A) | MCCB-S-LV | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with circuit breaker closed and across each open pole
Operation | Operate circuit breaker auxiliary and control devices such as local and remote-control switches, shunt trips coils, close coils, motors, auxiliary switches, and under-voltage coils
Calibration | Verify the calibration of all functions of the trip unit by means of the manufacturer’s specified test set for circuit breakers equipped with electronic trip units
Trip | Perform inverse time trip test at 300% of rated continuous current of thermal magnetic circuit breakers
Trip | Perform inverse time trip test at 300% of rated continuous current of electronic trip circuit breakers
Trip | Perform the instantaneous overcurrent trip test for thermal-magnetic circuit breakers by “run-up” or “pulse” method
Trip | Perform the instantaneous overcurrent trip test for electronic trip breakers by “run-up” or “pulse” method
Rated hold-in | Perform rated hold-in test
Current-limiter resistance | Test current-limiter resistance
Rating plug battery | Check status of rating plug battery
Millivolt drop | Perform millivolt drop test
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Low-Voltage Molded Case Circuit Breaker (> 250A) | MCCB-L-LV | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with circuit breaker closed and across each open pole
Operation | Operate circuit breaker auxiliary and control devices such as local and remote-control switches, shunt trips coils, close coils, motors, auxiliary switches, and under-voltage coils
Calibration | Verify the calibration of all functions of the trip unit by means of the manufacturer’s specified test set for circuit breakers equipped with electronic trip units
Trip | Perform inverse time trip test at 300% of rated continuous current of thermal magnetic circuit breakers
Trip | Perform inverse time trip test at 300% of rated continuous current of electronic trip circuit breakers
Trip | Perform the instantaneous overcurrent trip test for thermal-magnetic circuit breakers by “run-up” or “pulse” method
Trip | Perform the instantaneous overcurrent trip test for electronic trip breakers by “run-up” or “pulse” method
Rated hold-in | Perform rated hold-in test
Current-limiter resistance | Test current-limiter resistance
Rating plug battery | Check status of rating plug battery
Millivolt drop | Perform millivolt drop test
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Low-Voltage Insulated Case Circuit Breaker | ICCB | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with circuit breaker closed and across each open pole
Operation | Operate circuit breaker auxiliary and control devices such as local and remote-control switches, shunt trips coils, close coils, motors, auxiliary switches, and under-voltage coils
Calibration | Verify the calibration of all functions of the trip unit by means of the manufacturer’s specified test set for circuit breakers equipped with electronic trip units
Trip | Perform inverse time trip test at 300% of rated continuous current of electronic trip circuit breakers
Trip | Perform the instantaneous overcurrent trip test for electronic trip breakers by “run-up” or “pulse” method
Rated hold-in | Perform rated hold-in test
Current-limiter resistance | Test current-limiter resistance
Rating plug battery | Check status of rating plug battery
Millivolt drop test | Perform millivolt drop test
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Low-Voltage Power Circuit Breaker | LVCB | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with circuit breaker closed and across each open pole
Operation | Operate circuit breaker auxiliary and control devices such as local and remote-control switches, shunt trips coils, close coils, motors, auxiliary switches, and under-voltage coils
Calibration | Verify the calibration of all functions of the trip unit by means of the manufacturer’s specified test set for circuit breakers equipped with electronic trip units
Trip | Perform inverse time trip test at 300% of rated continuous current of electronic trip circuit breakers
Trip | Perform the instantaneous overcurrent trip test for thermal-magnetic circuit breakers by “run-up” or “pulse” method
Trip | Perform the instantaneous overcurrent trip test for electronic trip breakers by “run-up” or “pulse” method
Rated hold-in | Perform rated hold-in test
Current-limiter resistance | Test current-limiter resistance
Rating plug battery | Check status of rating plug battery
Millivolt drop test | Perform millivolt drop test
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Inspect electrical connections for high resistance |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Medium-Voltage Air Magnetic Circuit Breaker | AMCB | 70B-ENHANCED | electricalTesting
Contact resistance | Measure contact resistance of each switching pole
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with circuit breaker closed and across each open pole
Control power | Verify control power for close and trip functions
Trip | Perform trip and close tests with control switch
Operation | Verify operating mechanism charge, anti-pump, and trip-free functions
Operation | Verify proper operation of space heaters, if equipped
AC Overpotential | Perform an ac overpotential test one pole at a time with the other poles and structure grounded
AC Overpotential | Perform an ac overpotential test on control wiring | WARNING: Do not perform this test on wiring connected to solid-state components.
Blow-out coil | Verify blow-out coil continuity
Motion analysis | Perform circuit breaker motion analysis
Contact timing | Perform circuit breaker contact timing test
Coil current | Perform trip/close coil current signature analysis
Pickup | Perform pickup test on trip and/or close coil
Power factor | Measure power/dissipation factor
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Inspect electrical connections for high resistance |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Medium-Voltage Vacuum Circuit Breaker | VCCB | 70B-ENHANCED | electricalTesting
Contact resistance | Measure contact resistance of each switching pole
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with circuit breaker closed and across each open pole
Control power | Verify control power for close and trip functions
Trip | Perform trip and close tests with control switch
Operation | Verify operating mechanism charge, anti-pump, and trip-free functions
Operation | Perform vacuum integrity test by ac overpotential across each vacuum bottle
AC Overpotential | Verify proper operation of space heaters, if equipped
AC Overpotential | Perform an ac overpotential test one pole at a time with the other poles and structure grounded
Blow-out coil | Perform an ac overpotential test on control wiring | WARNING: Do not perform this test on wiring connected to solid-state components.
Motion analysis | Perform circuit breaker motion analysis
Contact timing | Perform circuit breaker contact timing test
Coil current | Perform trip/close coil current signature analysis
Pickup | Perform pickup test on trip and/or close coil
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Inspect electrical connections for high resistance |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Medim-Votlage Gas Insulated Circuit Breaker | GICB | 70B-ENHANCED | electricalTesting
Contact resistance | Measure contact resistance of each switching pole
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with circuit breaker closed and across each open pole
Control power | Verify control power for close and trip functions
Trip | Perform trip and close tests with control switch
Operation | Verify operating mechanism charge, anti-pump, and trip-free functions
Operation | Verify proper operation of space heaters, if equipped
AC Overpotential | Perform an ac overpotential test one pole at a time with the other poles and structure grounded
AC Overpotential | Perform an ac overpotential test on control wiring | WARNING: Do not perform this test on wiring connected to solid-state components.
Blow-out coil | Perform circuit breaker motion analysis
Motion analysis | Perform circuit breaker contact timing test
Contact timing | Perform trip/close coil current signature analysis
Coil current | Perform pickup test on trip and/or close coil
Pickup | Measure power/dissipation factor
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Inspect electrical connections for high resistance |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Medium-Voltage Oil Insulated Circuit Breaker | OICB | 70B-ENHANCED | electricalTesting
Contact resistance | Measure contact resistance of each switching pole
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with circuit breaker closed and across each open pole
Control power | Verify control power for close and trip functions
Trip | Perform trip and close tests with control switch
Operation | Verify operating mechanism charge, anti-pump, and trip-free functions
Operation | Verify proper operation of space heaters, if equipped
AC Overpotential | Perform an ac overpotential test one pole at a time with the other poles and structure grounded
AC Overpotential | Perform an ac overpotential test on control wiring | WARNING: Do not perform this test on wiring connected to solid-state components.
Blow-out coil | Perform circuit breaker motion analysis
Motion analysis | Perform circuit breaker contact timing test
Contact timing | Perform trip/close coil current signature analysis
Coil current | Perform pickup test on trip and/or close coil
Pickup | Measure power/dissipation factor
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Operation | Operate circuit breaker auxiliary and control devices such as local and remote-control switches, shunt trips coils, close coils, motors, auxiliary switches, and under-voltage coils |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Low-Voltage Molded Case Circuit Breaker (<= 250A) | MCCB-S-LV | 70B-STANDARD | electricalTesting
Current-limiter resistance | Test current-limiter resistance
Rating plug battery | Check status of rating plug battery
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Low-Voltage Molded Case Circuit Breaker (> 250A) | MCCB-L-LV | 70B-STANDARD | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with circuit breaker closed and across each open pole
Operation | Operate circuit breaker auxiliary and control devices such as local and remote-control switches, shunt trips coils, close coils, motors, auxiliary switches, and under-voltage coils
Calibration | Verify the calibration of all functions of the trip unit by means of the manufacturer’s specified test set for circuit breakers equipped with electronic trip units
Trip | Perform inverse time trip test at 300% of rated continuous current of thermal magnetic circuit breakers
Trip | Perform the instantaneous overcurrent trip test for thermal-magnetic circuit breakers by “run-up” or “pulse” method
Rated hold-in | Perform rated hold-in test
Current-limiter resistance | Test current-limiter resistance
Rating plug battery | Check status of rating plug battery
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Low-Voltage Insulated Case Circuit Breaker | ICCB | 70B-STANDARD | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with circuit breaker closed and across each open pole
Operation | Operate circuit breaker auxiliary and control devices such as local and remote-control switches, shunt trips coils, close coils, motors, auxiliary switches, and under-voltage coils
Calibration | Verify the calibration of all functions of the trip unit by means of the manufacturer’s specified test set for circuit breakers equipped with electronic trip units
Current-limiter resistance | Test current-limiter resistance
Rating plug battery | Check status of rating plug battery
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Low-Voltage Power Circuit Breaker | LVCB | 70B-STANDARD | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with circuit breaker closed and across each open pole
Operation | Operate circuit breaker auxiliary and control devices such as local and remote-control switches, shunt trips coils, close coils, motors, auxiliary switches, and under-voltage coils
Calibration | Verify the calibration of all functions of the trip unit by means of the manufacturer’s specified test set for circuit breakers equipped with electronic trip units
Trip | Perform the instantaneous overcurrent trip test for thermal-magnetic circuit breakers by “run-up” or “pulse” method
Current-limiter resistance | Test current-limiter resistance
Rating plug battery | Check status of rating plug battery
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Inspect electrical connections for high resistance |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Medium-Voltage Air Magnetic Circuit Breaker | AMCB | 70B-STANDARD | electricalTesting
Contact resistance | Measure contact resistance of each switching pole
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with circuit breaker closed and across each open pole
Control power | Verify control power for close and trip functions
Trip | Perform trip and close tests with control switch
Operating mechanism | Verify operating mechanism charge, anti-pump, and trip-free functions
Operation | Verify proper operation of space heaters, if equipped
Blow-out coil | Verify blow-out coil continuity
Contact | Perform circuit breaker contact timing test
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Inspect electrical connections for high resistance |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Medium-Voltage Vacuum Circuit Breaker | VCCB | 70B-STANDARD | electricalTesting
Contact resistance | Measure contact resistance of each switching pole
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with circuit breaker closed and across each open pole
Control power | Verify control power for close and trip functions
Trip | Perform trip and close tests with control switch
Operating mechanism | Verify operating mechanism charge, anti-pump, and trip-free functions
Vacuum | Perform vacuum integrity test by ac overpotential across each vacuum bottle
Operation | Verify proper operation of space heaters, if equipped
Motion analysis | Perform circuit breaker motion analysis
Contact | Perform circuit breaker contact timing test
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Inspect electrical connections for high resistance |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Medim-Votlage Gas Insulated Circuit Breaker | GICB | 70B-STANDARD | electricalTesting
Contact resistance | Measure contact resistance of each switching pole
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with circuit breaker closed and across each open pole
Control power | Verify control power for close and trip functions
Trip | Perform trip and close tests with control switch
Operating mechanism | Verify operating mechanism charge, anti-pump, and trip-free functions
Operation | Verify proper operation of space heaters, if equipped
Motion analysis | Perform circuit breaker motion analysis
Contact | Perform circuit breaker contact timing test
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Inspect electrical connections for high resistance |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Medium-Voltage Oil Insulated Circuit Breaker | OICB | 70B-STANDARD | electricalTesting
Contact resistance | Measure contact resistance of each switching pole
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with circuit breaker closed and across each open pole
Control power | Verify control power for close and trip functions
Trip | Perform trip and close tests with control switch
Operating mechanism | Verify operating mechanism charge, anti-pump, and trip-free functions
Operation | Verify proper operation of space heaters, if equipped
Motion analysis | Perform circuit breaker motion analysis
Contact | Perform circuit breaker contact timing test
Power factor | Measure power/dissipation factor

## ch.16
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Discoloration | Check for discoloration of fuse terminals and clips caused by heat |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Fuse (<= 1000V) | FUSE-LV | 70B-ENHANCED | visualInspection
Indicating devices | Check fuse indicating device status, if applicable
Catalog numbers | Confirm that fuses, in any one circuit, have the same catalog number to ensure that they have the same current rating, voltage rating, interrupting rating, time delay, and type (e.g., UL class)
Study matching | Confirm that all fuses match the most recent short-circuit, coordination, and arc flash studies
Rejection type matching | Where current-limiting fuses are required, confirm that correct rejection-type mountings are used so that the current-limiting fuses cannot be replaced by non-current-limiting fuses
Ratings | Verify ratings for correct system application
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Discoloration | Check for discoloration of fuse terminals and clips caused by heat |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Fuse (> 1000V) | FUSE-MV | 70B-ENHANCED | visualInspection
Indicating devices | Check fuse indicating device status, if applicable
Catalog numbers | Confirm that fuses, in any one circuit, have the same catalog number to ensure that they have the same current rating, voltage rating, interrupting rating, time delay, and type (e.g., UL class)
Study matching | Confirm that all fuses match the most recent short-circuit, coordination, and arc flash studies
Rejection type matching | Where current-limiting fuses are required, confirm that correct rejection-type mountings are used so that the current-limiting fuses cannot be replaced by non-current-limiting fuses
Ratings | Verify ratings for correct system application
Insulators | Inspect insulators for breaks, cracks, tracking, corona, burns, or overheating
Contact surfaces | Inspect contact surfaces for pitting or burning, alignment, and contact pressure
Fuse unit | Examine the fuse unit, fuse tube, and renewable element, if used, for evidence of corrosion and wear
Bolts | Inspect bolts, nuts, washers, pins, and terminal connectors to ensure they are in place, in good condition, and properly installed
Seals | Inspect seals of vented expulsion type fuses
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Discoloration | Check for discoloration of fuse terminals and clips caused by heat |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Fuse (<= 1000V) | FUSE-LV | 70B-STANDARD | visualInspection
Indicating devices | Check fuse indicating device status, if applicable
Catalog numbers | Confirm that fuses, in any one circuit, have the same catalog number to ensure that they have the same current rating, voltage rating, interrupting rating, time delay, and type (e.g., UL class)
Study matching | Confirm that all fuses match the most recent short-circuit, coordination, and arc flash studies
Rejection type matching | Where current-limiting fuses are required, confirm that correct rejection-type mountings are used so that the current-limiting fuses cannot be replaced by non-current-limiting fuses
Ratings | Verify ratings for correct system application
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Discoloration | Check for discoloration of fuse terminals and clips caused by heat |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Fuse (> 1000V) | FUSE-MV | 70B-STANDARD | visualInspection
Indicating devices | Check fuse indicating device status, if applicable
Catalog numbers | Confirm that fuses, in any one circuit, have the same catalog number to ensure that they have the same current rating, voltage rating, interrupting rating, time delay, and type (e.g., UL class)
Study matching | Confirm that all fuses match the most recent short-circuit, coordination, and arc flash studies
Rejection type matching | Where current-limiting fuses are required, confirm that correct rejection-type mountings are used so that the current-limiting fuses cannot be replaced by non-current-limiting fuses
Ratings | Verify ratings for correct system application
Insulators | Inspect insulators for breaks, cracks, tracking, corona, burns, or overheating
Fuse unit | Examine the fuse unit, fuse tube, and renewable element, if used, for evidence of corrosion and wear
Bolts | Inspect bolts, nuts, washers, pins, and terminal connectors to ensure they are in place, in good condition, and properly installed
Seals | Inspect seals of vented expulsion type fuses
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Discoloration | Check for discoloration of fuse terminals and clips caused by heat |  | Basic Energized Visual Inspection Form | Fuse (<= 1000V) | FUSE-LV | BASIC | visualInspection
Indicating devices | Check fuse indicating device status, if applicable
Catalog numbers | Confirm that fuses, in any one circuit, have the same catalog number to ensure that they have the same current rating, voltage rating, interrupting rating, time delay, and type (e.g., UL class)
Study matching | Confirm that all fuses match the most recent short-circuit, coordination, and arc flash studies
Ratings | Verify ratings for correct system application
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Discoloration | Check for discoloration of fuse terminals and clips caused by heat |  | Basic Energized Visual Inspection Form | Fuse (> 1000V) | FUSE-MV | BASIC | visualInspection
Indicating devices | Check fuse indicating device status, if applicable
Catalog numbers | Confirm that fuses, in any one circuit, have the same catalog number to ensure that they have the same current rating, voltage rating, interrupting rating, time delay, and type (e.g., UL class)
Study matching | Confirm that all fuses match the most recent short-circuit, coordination, and arc flash studies
Ratings | Verify ratings for correct system application
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean fuse terminals and clips that have become corroded or oxidized |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Fuse (<= 1000V) | FUSE-LV | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean fuse terminals and clips that have become corroded or oxidized |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Fuse (> 1000V) | FUSE-MV | 70B-ENHANCED | cleaning
Cleanliness | Clean insulators of accumulated dust and foreign matter
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean fuse terminals and clips that have become corroded or oxidized |  | NFPA 70B® Standard De-Energized Cleaning Form | Fuse (<= 1000V) | FUSE-LV | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean fuse terminals and clips that have become corroded or oxidized |  | NFPA 70B® Standard De-Energized Cleaning Form | Fuse (> 1000V) | FUSE-MV | 70B-STANDARD | cleaning
Cleanliness | Clean insulators of accumulated dust and foreign matter
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Tightness | Check fuse holder terminations for tightness |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Fuse (<= 1000V) | FUSE-LV | 70B-ENHANCED | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Check fuse holder terminations for tightness |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Fuse (> 1000V) | FUSE-MV | 70B-ENHANCED | mechanicalServicing
Cleanliness | Verify that each fuseholder has adequate mechanical support
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Tightness | Check fuse holder terminations for tightness |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Fuse (<= 1000V) | FUSE-LV | 70B-STANDARD | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Tightness | Check fuse holder terminations for tightness |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Fuse (> 1000V) | FUSE-MV | 70B-STANDARD | mechanicalServicing
Tightness | Verify that each fuseholder has adequate mechanical support
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure fuse connection resistance |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Fuse (<= 1000V) | FUSE-LV | 70B-ENHANCED | electricalTesting
Fuse resistance | Measure fuse resistance
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure fuse connection resistance |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Fuse (> 1000V) | FUSE-MV | 70B-ENHANCED | electricalTesting
Fuse resistance | Measure fuse resistance
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure fuse connection resistance |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Fuse (> 1000V) | FUSE-MV | 70B-STANDARD | electricalTesting
Fuse resistance | Measure fuse resistance

## ch.17
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Disconnect Switch (<= 1000V) | DISC-LV | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Contacts | Check that exposed switch contacts, both moving and stationary, are free from environmental contamination
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Contacts | Examine switches with exposed contacts for evidence of high short-circuit closing operation
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Fused Disconnect Switch (<= 1000V) | DISC-F-LV | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Contacts | Check that exposed switch contacts, both moving and stationary, are free from environmental contamination
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Contacts | Examine switches with exposed contacts for evidence of high short-circuit closing operation
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Transfer Switch (<= 1000V) | MTSW-LV | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Contacts | Check that exposed switch contacts, both moving and stationary, are free from environmental contamination
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Contacts | Examine switches with exposed contacts for evidence of high short-circuit closing operation
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Automatic Transfer Switch (<= 1000V) | ATSW-LV | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Contacts | Check that exposed switch contacts, both moving and stationary, are free from environmental contamination
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Contacts | Examine switches with exposed contacts for evidence of high short-circuit closing operation
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Bolted-Pressure Switch (BPS) | BPSW | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Contacts | Check that exposed switch contacts, both moving and stationary, are free from environmental contamination
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Contacts | Examine switches with exposed contacts for evidence of high short-circuit closing operation
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | High-Pressure Contact Switch (HPC) | HPSW | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Contacts | Check that exposed switch contacts, both moving and stationary, are free from environmental contamination
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Contacts | Examine switches with exposed contacts for evidence of high short-circuit closing operation
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Bypass-Isolation Switch (<= 1000V) | BISW-LV | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Contacts | Check that exposed switch contacts, both moving and stationary, are free from environmental contamination
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Contacts | Examine switches with exposed contacts for evidence of high short-circuit closing operation
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Disconnect Switch (> 1000V) | DISC-MV | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
Arc chutes | Inspect each arc chute for cracks or excessive erosion
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Fused Disconnect Switch (>1000V) | DISC-F-MV | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
Arc chutes | Inspect each arc chute for cracks or excessive erosion
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Transfer Switch (> 1000V) | MTSW-MV | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
Arc chutes | Inspect each arc chute for cracks or excessive erosion
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Automatic Transfer Switch (> 1000V) | ATSW-MV | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
Arc chutes | Inspect each arc chute for cracks or excessive erosion
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Load-Interruptor Switch | LISW | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
Arc chutes | Inspect each arc chute for cracks or excessive erosion
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Bypass-Isolation Switch (> 1000V) | BISW-MV | 70B-ENHANCED | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
Arc chutes | Inspect each arc chute for cracks or excessive erosion
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Disconnect Switch (<= 1000V) | DISC-LV | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Contacts | Check that exposed switch contacts, both moving and stationary, are free from environmental contamination
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Contacts | Examine switches with exposed contacts for evidence of high short-circuit closing operation
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Fused Disconnect Switch (<= 1000V) | DISC-F-LV | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Contacts | Check that exposed switch contacts, both moving and stationary, are free from environmental contamination
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Contacts | Examine switches with exposed contacts for evidence of high short-circuit closing operation
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Transfer Switch (<= 1000V) | MTSW-LV | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Contacts | Check that exposed switch contacts, both moving and stationary, are free from environmental contamination
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Contacts | Examine switches with exposed contacts for evidence of high short-circuit closing operation
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Automatic Transfer Switch (<= 1000V) | ATSW-LV | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Contacts | Check that exposed switch contacts, both moving and stationary, are free from environmental contamination
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Contacts | Examine switches with exposed contacts for evidence of high short-circuit closing operation
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Bolted-Pressure Switch (BPS) | BPSW | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Contacts | Check that exposed switch contacts, both moving and stationary, are free from environmental contamination
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Contacts | Examine switches with exposed contacts for evidence of high short-circuit closing operation
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Standard De-Energized Visual Inspection Form | High-Pressure Contact Switch (HPC) | HPSW | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Contacts | Check that exposed switch contacts, both moving and stationary, are free from environmental contamination
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Contacts | Examine switches with exposed contacts for evidence of high short-circuit closing operation
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Bypass-Isolation Switch (<= 1000V) | BISW-LV | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Contacts | Check that exposed switch contacts, both moving and stationary, are free from environmental contamination
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Contacts | Examine switches with exposed contacts for evidence of high short-circuit closing operation
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Disconnect Switch (> 1000V) | DISC-MV | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
Arc chutes | Inspect each arc chute for cracks or excessive erosion
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Fused Disconnect Switch (>1000V) | DISC-F-MV | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
Arc chutes | Inspect each arc chute for cracks or excessive erosion
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Transfer Switch (> 1000V) | MTSW-MV | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
Arc chutes | Inspect each arc chute for cracks or excessive erosion
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Automatic Transfer Switch (> 1000V) | ATSW-MV | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
Arc chutes | Inspect each arc chute for cracks or excessive erosion
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Load-Interruptor Switch | LISW | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
Arc chutes | Inspect each arc chute for cracks or excessive erosion
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Bypass-Isolation Switch (> 1000V) | BISW-MV | 70B-STANDARD | visualInspection
Insulating materials | Inspect insulating materials and switch base for evidence of physical damage, cracks from stresses of operation, or contamination
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition, including corrosion
Current-carrying parts | Inspect visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Fuses | Check that fuses are secured
Blades | Check the main body of the switch blades and the arcing contacts for arc erosion | Mild pitting and burning is permitted.
Arc chutes | Inspect each arc chute for cracks or excessive erosion
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | Basic Energized Visual Inspection Form | Disconnect Switch (<= 1000V) | DISC-LV | BASIC | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | Basic Energized Visual Inspection Form | Fused Disconnect Switch (<= 1000V) | DISC-F-LV | BASIC | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | Basic Energized Visual Inspection Form | Transfer Switch (<= 1000V) | MTSW-LV | BASIC | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | Basic Energized Visual Inspection Form | Automatic Transfer Switch (<= 1000V) | ATSW-LV | BASIC | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | Basic Energized Visual Inspection Form | Bolted-Pressure Switch (BPS) | BPSW | BASIC | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | Basic Energized Visual Inspection Form | High-Pressure Contact Switch (HPC) | HPSW | BASIC | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | Basic Energized Visual Inspection Form | Bypass-Isolation Switch (<= 1000V) | BISW-LV | BASIC | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | Basic Energized Visual Inspection Form | Disconnect Switch (> 1000V) | DISC-MV | BASIC | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | Basic Energized Visual Inspection Form | Fused Disconnect Switch (>1000V) | DISC-F-MV | BASIC | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | Basic Energized Visual Inspection Form | Transfer Switch (> 1000V) | MTSW-MV | BASIC | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | Basic Energized Visual Inspection Form | Automatic Transfer Switch (> 1000V) | ATSW-MV | BASIC | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | Basic Energized Visual Inspection Form | Load-Interruptor Switch | LISW | BASIC | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors and latches | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | Basic Energized Visual Inspection Form | Bypass-Isolation Switch (> 1000V) | BISW-MV | BASIC | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Disconnect Switch (<= 1000V) | DISC-LV | 70B-ENHANCED | cleaning
Cleanliness | Clean exposed switch contacts with a multi-purpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Fused Disconnect Switch (<= 1000V) | DISC-F-LV | 70B-ENHANCED | cleaning
Cleanliness | Clean exposed switch contacts with a multi-purpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Transfer Switch (<= 1000V) | MTSW-LV | 70B-ENHANCED | cleaning
Cleanliness | Clean exposed switch contacts with a multi-purpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Automatic Transfer Switch (<= 1000V) | ATSW-LV | 70B-ENHANCED | cleaning
Cleanliness | Clean exposed switch contacts with a multi-purpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Bolted-Pressure Switch (BPS) | BPSW | 70B-ENHANCED | cleaning
Cleanliness | Clean exposed switch contacts with a multi-purpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Enhanced De-Energized Cleaning Form | High-Pressure Contact Switch (HPC) | HPSW | 70B-ENHANCED | cleaning
Cleanliness | Clean exposed switch contacts with a multi-purpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Bypass-Isolation Switch (<= 1000V) | BISW-LV | 70B-ENHANCED | cleaning
Cleanliness | Clean exposed switch contacts with a multi-purpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Disconnect Switch (> 1000V) | DISC-MV | 70B-ENHANCED | cleaning
Cleanliness | Wipe contact surfaces with a noncorrosive cleaning agent
Cleanliness | Clean insulators
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Fused Disconnect Switch (>1000V) | DISC-F-MV | 70B-ENHANCED | cleaning
Cleanliness | Wipe contact surfaces with a noncorrosive cleaning agent
Cleanliness | Clean insulators
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Transfer Switch (> 1000V) | MTSW-MV | 70B-ENHANCED | cleaning
Cleanliness | Wipe contact surfaces with a noncorrosive cleaning agent
Cleanliness | Clean insulators
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Automatic Transfer Switch (> 1000V) | ATSW-MV | 70B-ENHANCED | cleaning
Cleanliness | Wipe contact surfaces with a noncorrosive cleaning agent
Cleanliness | Clean insulators
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Load-Interruptor Switch | LISW | 70B-ENHANCED | cleaning
Cleanliness | Wipe contact surfaces with a noncorrosive cleaning agent
Cleanliness | Clean insulators
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Bypass-Isolation Switch (> 1000V) | BISW-MV | 70B-ENHANCED | cleaning
Cleanliness | Wipe contact surfaces with a noncorrosive cleaning agent
Cleanliness | Clean insulators
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Standard De-Energized Cleaning Form | Disconnect Switch (<= 1000V) | DISC-LV | 70B-STANDARD | cleaning
Cleanliness | Clean exposed switch contacts with a multi-purpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Standard De-Energized Cleaning Form | Fused Disconnect Switch (<= 1000V) | DISC-F-LV | 70B-STANDARD | cleaning
Cleanliness | Clean exposed switch contacts with a multi-purpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Standard De-Energized Cleaning Form | Transfer Switch (<= 1000V) | MTSW-LV | 70B-STANDARD | cleaning
Cleanliness | Clean exposed switch contacts with a multi-purpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Standard De-Energized Cleaning Form | Automatic Transfer Switch (<= 1000V) | ATSW-LV | 70B-STANDARD | cleaning
Cleanliness | Clean exposed switch contacts with a multi-purpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Standard De-Energized Cleaning Form | Bolted-Pressure Switch (BPS) | BPSW | 70B-STANDARD | cleaning
Cleanliness | Clean exposed switch contacts with a multi-purpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Standard De-Energized Cleaning Form | High-Pressure Contact Switch (HPC) | HPSW | 70B-STANDARD | cleaning
Cleanliness | Clean exposed switch contacts with a multi-purpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Standard De-Energized Cleaning Form | Bypass-Isolation Switch (<= 1000V) | BISW-LV | 70B-STANDARD | cleaning
Cleanliness | Clean exposed switch contacts with a multi-purpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Standard De-Energized Cleaning Form | Disconnect Switch (> 1000V) | DISC-MV | 70B-STANDARD | cleaning
Cleanliness | Wipe contact surfaces with a noncorrosive cleaning agent
Cleanliness | Clean insulators
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Standard De-Energized Cleaning Form | Fused Disconnect Switch (>1000V) | DISC-F-MV | 70B-STANDARD | cleaning
Cleanliness | Wipe contact surfaces with a noncorrosive cleaning agent
Cleanliness | Clean insulators
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Standard De-Energized Cleaning Form | Transfer Switch (> 1000V) | MTSW-MV | 70B-STANDARD | cleaning
Cleanliness | Wipe contact surfaces with a noncorrosive cleaning agent
Cleanliness | Clean insulators
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Standard De-Energized Cleaning Form | Automatic Transfer Switch (> 1000V) | ATSW-MV | 70B-STANDARD | cleaning
Cleanliness | Wipe contact surfaces with a noncorrosive cleaning agent
Cleanliness | Clean insulators
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Standard De-Energized Cleaning Form | Load-Interruptor Switch | LISW | 70B-STANDARD | cleaning
Cleanliness | Wipe contact surfaces with a noncorrosive cleaning agent
Cleanliness | Clean insulators
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the switch and barriers |  | NFPA 70B® Standard De-Energized Cleaning Form | Bypass-Isolation Switch (> 1000V) | BISW-MV | 70B-STANDARD | cleaning
Cleanliness | Wipe contact surfaces with a noncorrosive cleaning agent
Cleanliness | Clean insulators
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed switch contacts. | Enclosed and dead-front (safety) switches do not require lubrication. | NFPA 70B® Enhanced De-Energized Lubrication Form | Disconnect Switch (<= 1000V) | DISC-LV | 70B-ENHANCED | lubrication
Lubrication | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed switch contacts. | Enclosed and dead-front (safety) switches do not require lubrication. | NFPA 70B® Enhanced De-Energized Lubrication Form | Fused Disconnect Switch (<= 1000V) | DISC-F-LV | 70B-ENHANCED | lubrication
Lubrication | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed switch contacts. | Enclosed and dead-front (safety) switches do not require lubrication. | NFPA 70B® Enhanced De-Energized Lubrication Form | Transfer Switch (<= 1000V) | MTSW-LV | 70B-ENHANCED | lubrication
Lubrication | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed switch contacts. | Enclosed and dead-front (safety) switches do not require lubrication. | NFPA 70B® Enhanced De-Energized Lubrication Form | Automatic Transfer Switch (<= 1000V) | ATSW-LV | 70B-ENHANCED | lubrication
Lubrication | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed switch contacts. | Enclosed and dead-front (safety) switches do not require lubrication. | NFPA 70B® Enhanced De-Energized Lubrication Form | Bolted-Pressure Switch (BPS) | BPSW | 70B-ENHANCED | lubrication
Lubrication | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed switch contacts. | Enclosed and dead-front (safety) switches do not require lubrication. | NFPA 70B® Enhanced De-Energized Lubrication Form | High-Pressure Contact Switch (HPC) | HPSW | 70B-ENHANCED | lubrication
Lubrication | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed switch contacts. | Enclosed and dead-front (safety) switches do not require lubrication. | NFPA 70B® Enhanced De-Energized Lubrication Form | Bypass-Isolation Switch (<= 1000V) | BISW-LV | 70B-ENHANCED | lubrication
Lubrication | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Disconnect Switch (> 1000V) | DISC-MV | 70B-ENHANCED | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Fused Disconnect Switch (>1000V) | DISC-F-MV | 70B-ENHANCED | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Transfer Switch (> 1000V) | MTSW-MV | 70B-ENHANCED | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Automatic Transfer Switch (> 1000V) | ATSW-MV | 70B-ENHANCED | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Load-Interruptor Switch | LISW | 70B-ENHANCED | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Bypass-Isolation Switch (> 1000V) | BISW-MV | 70B-ENHANCED | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed switch contacts. | Enclosed and dead-front (safety) switches do not require lubrication. | NFPA 70B® Standard De-Energized Lubrication Form | Disconnect Switch (<= 1000V) | DISC-LV | 70B-STANDARD | lubrication
Lubrication | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed switch contacts. | Enclosed and dead-front (safety) switches do not require lubrication. | NFPA 70B® Standard De-Energized Lubrication Form | Fused Disconnect Switch (<= 1000V) | DISC-F-LV | 70B-STANDARD | lubrication
Lubrication | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed switch contacts. | Enclosed and dead-front (safety) switches do not require lubrication. | NFPA 70B® Standard De-Energized Lubrication Form | Transfer Switch (<= 1000V) | MTSW-LV | 70B-STANDARD | lubrication
Lubrication | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed switch contacts. | Enclosed and dead-front (safety) switches do not require lubrication. | NFPA 70B® Standard De-Energized Lubrication Form | Automatic Transfer Switch (<= 1000V) | ATSW-LV | 70B-STANDARD | lubrication
Lubrication | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed switch contacts. | Enclosed and dead-front (safety) switches do not require lubrication. | NFPA 70B® Standard De-Energized Lubrication Form | Bolted-Pressure Switch (BPS) | BPSW | 70B-STANDARD | lubrication
Lubrication | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed switch contacts. | Enclosed and dead-front (safety) switches do not require lubrication. | NFPA 70B® Standard De-Energized Lubrication Form | High-Pressure Contact Switch (HPC) | HPSW | 70B-STANDARD | lubrication
Lubrication | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed switch contacts. | Enclosed and dead-front (safety) switches do not require lubrication. | NFPA 70B® Standard De-Energized Lubrication Form | Bypass-Isolation Switch (<= 1000V) | BISW-LV | 70B-STANDARD | lubrication
Lubrication | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces. |  | NFPA 70B® Standard De-Energized Lubrication Form | Disconnect Switch (> 1000V) | DISC-MV | 70B-STANDARD | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces. |  | NFPA 70B® Standard De-Energized Lubrication Form | Fused Disconnect Switch (>1000V) | DISC-F-MV | 70B-STANDARD | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces. |  | NFPA 70B® Standard De-Energized Lubrication Form | Transfer Switch (> 1000V) | MTSW-MV | 70B-STANDARD | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces. |  | NFPA 70B® Standard De-Energized Lubrication Form | Automatic Transfer Switch (> 1000V) | ATSW-MV | 70B-STANDARD | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces. |  | NFPA 70B® Standard De-Energized Lubrication Form | Load-Interruptor Switch | LISW | 70B-STANDARD | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces. |  | NFPA 70B® Standard De-Energized Lubrication Form | Bypass-Isolation Switch (> 1000V) | BISW-MV | 70B-STANDARD | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Disconnect Switch (<= 1000V) | DISC-LV | 70B-ENHANCED | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Operate the switch three times to work the lubricant between the contacts
Operation | Verify operation and alignment of mechanical interlocks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Fused Disconnect Switch (<= 1000V) | DISC-F-LV | 70B-ENHANCED | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Operate the switch three times to work the lubricant between the contacts
Operation | Verify operation and alignment of mechanical interlocks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Transfer Switch (<= 1000V) | MTSW-LV | 70B-ENHANCED | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Operate the switch three times to work the lubricant between the contacts
Operation | Verify operation and alignment of mechanical interlocks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Automatic Transfer Switch (<= 1000V) | ATSW-LV | 70B-ENHANCED | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Operate the switch three times to work the lubricant between the contacts
Operation | Verify operation and alignment of mechanical interlocks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Bolted-Pressure Switch (BPS) | BPSW | 70B-ENHANCED | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Operate the switch three times to work the lubricant between the contacts
Operation | Verify operation and alignment of mechanical interlocks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | High-Pressure Contact Switch (HPC) | HPSW | 70B-ENHANCED | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Operate the switch three times to work the lubricant between the contacts
Operation | Verify operation and alignment of mechanical interlocks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Bypass-Isolation Switch (<= 1000V) | BISW-LV | 70B-ENHANCED | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Operate the switch three times to work the lubricant between the contacts
Operation | Verify operation and alignment of mechanical interlocks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Disconnect Switch (<= 1000V) | DISC-LV | 70B-ENHANCED | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Verify operation and alignment of mechanical interlocks
Contact pressure | Verify the contact pressure is within specification using a force gauge or other device that measures forces
Operation | With the door closed and latched, close and open the switch three times to confirm the switch and operator lever is operating; view switch position through the window after each operation, where available; when open, verify that switch blades have cleared the arc chutes; when closed, verify that the switch blades are inside the arc chutes and vertical; if they are not, perform alignment adjustments per the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Fused Disconnect Switch (>1000V) | DISC-F-MV | 70B-ENHANCED | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Verify operation and alignment of mechanical interlocks
Contact pressure | Verify the contact pressure is within specification using a force gauge or other device that measures forces
Operation | With the door closed and latched, close and open the switch three times to confirm the switch and operator lever is operating; view switch position through the window after each operation, where available; when open, verify that switch blades have cleared the arc chutes; when closed, verify that the switch blades are inside the arc chutes and vertical; if they are not, perform alignment adjustments per the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Transfer Switch (> 1000V) | MTSW-MV | 70B-ENHANCED | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Verify operation and alignment of mechanical interlocks
Contact pressure | Verify the contact pressure is within specification using a force gauge or other device that measures forces
Operation | With the door closed and latched, close and open the switch three times to confirm the switch and operator lever is operating; view switch position through the window after each operation, where available; when open, verify that switch blades have cleared the arc chutes; when closed, verify that the switch blades are inside the arc chutes and vertical; if they are not, perform alignment adjustments per the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Automatic Transfer Switch (> 1000V) | ATSW-MV | 70B-ENHANCED | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Verify operation and alignment of mechanical interlocks
Contact pressure | Verify the contact pressure is within specification using a force gauge or other device that measures forces
Operation | With the door closed and latched, close and open the switch three times to confirm the switch and operator lever is operating; view switch position through the window after each operation, where available; when open, verify that switch blades have cleared the arc chutes; when closed, verify that the switch blades are inside the arc chutes and vertical; if they are not, perform alignment adjustments per the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Load-Interruptor Switch | LISW | 70B-ENHANCED | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Verify operation and alignment of mechanical interlocks
Contact pressure | Verify the contact pressure is within specification using a force gauge or other device that measures forces
Operation | With the door closed and latched, close and open the switch three times to confirm the switch and operator lever is operating; view switch position through the window after each operation, where available; when open, verify that switch blades have cleared the arc chutes; when closed, verify that the switch blades are inside the arc chutes and vertical; if they are not, perform alignment adjustments per the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Bypass-Isolation Switch (> 1000V) | BISW-MV | 70B-ENHANCED | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Verify operation and alignment of mechanical interlocks
Contact pressure | Verify the contact pressure is within specification using a force gauge or other device that measures forces
Operation | With the door closed and latched, close and open the switch three times to confirm the switch and operator lever is operating; view switch position through the window after each operation, where available; when open, verify that switch blades have cleared the arc chutes; when closed, verify that the switch blades are inside the arc chutes and vertical; if they are not, perform alignment adjustments per the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Disconnect Switch (<= 1000V) | DISC-LV | 70B-STANDARD | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Operate the switch three times to work the lubricant between the contacts
Operation | Verify operation and alignment of mechanical interlocks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Fused Disconnect Switch (<= 1000V) | DISC-F-LV | 70B-STANDARD | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Operate the switch three times to work the lubricant between the contacts
Operation | Verify operation and alignment of mechanical interlocks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Transfer Switch (<= 1000V) | MTSW-LV | 70B-STANDARD | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Operate the switch three times to work the lubricant between the contacts
Operation | Verify operation and alignment of mechanical interlocks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Automatic Transfer Switch (<= 1000V) | ATSW-LV | 70B-STANDARD | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Operate the switch three times to work the lubricant between the contacts
Operation | Verify operation and alignment of mechanical interlocks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Bolted-Pressure Switch (BPS) | BPSW | 70B-STANDARD | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Operate the switch three times to work the lubricant between the contacts
Operation | Verify operation and alignment of mechanical interlocks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | High-Pressure Contact Switch (HPC) | HPSW | 70B-STANDARD | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Operate the switch three times to work the lubricant between the contacts
Operation | Verify operation and alignment of mechanical interlocks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Bypass-Isolation Switch (<= 1000V) | BISW-LV | 70B-STANDARD | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Operate the switch three times to work the lubricant between the contacts
Operation | Verify operation and alignment of mechanical interlocks
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Disconnect Switch (<= 1000V) | DISC-LV | 70B-STANDARD | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Verify operation and alignment of mechanical interlocks
Contact pressure | Verify the contact pressure is within specification using a force gauge or other device that measures forces
Operation | With the door closed and latched, close and open the switch three times to confirm the switch and operator lever is operating; view switch position through the window after each operation, where available; when open, verify that switch blades have cleared the arc chutes; when closed, verify that the switch blades are inside the arc chutes and vertical; if they are not, perform alignment adjustments per the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Fused Disconnect Switch (>1000V) | DISC-F-MV | 70B-STANDARD | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Verify operation and alignment of mechanical interlocks
Contact pressure | Verify the contact pressure is within specification using a force gauge or other device that measures forces
Operation | With the door closed and latched, close and open the switch three times to confirm the switch and operator lever is operating; view switch position through the window after each operation, where available; when open, verify that switch blades have cleared the arc chutes; when closed, verify that the switch blades are inside the arc chutes and vertical; if they are not, perform alignment adjustments per the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Transfer Switch (> 1000V) | MTSW-MV | 70B-STANDARD | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Verify operation and alignment of mechanical interlocks
Contact pressure | Verify the contact pressure is within specification using a force gauge or other device that measures forces
Operation | With the door closed and latched, close and open the switch three times to confirm the switch and operator lever is operating; view switch position through the window after each operation, where available; when open, verify that switch blades have cleared the arc chutes; when closed, verify that the switch blades are inside the arc chutes and vertical; if they are not, perform alignment adjustments per the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Automatic Transfer Switch (> 1000V) | ATSW-MV | 70B-STANDARD | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Verify operation and alignment of mechanical interlocks
Contact pressure | Verify the contact pressure is within specification using a force gauge or other device that measures forces
Operation | With the door closed and latched, close and open the switch three times to confirm the switch and operator lever is operating; view switch position through the window after each operation, where available; when open, verify that switch blades have cleared the arc chutes; when closed, verify that the switch blades are inside the arc chutes and vertical; if they are not, perform alignment adjustments per the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Load-Interruptor Switch | LISW | 70B-STANDARD | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Verify operation and alignment of mechanical interlocks
Contact pressure | Verify the contact pressure is within specification using a force gauge or other device that measures forces
Operation | With the door closed and latched, close and open the switch three times to confirm the switch and operator lever is operating; view switch position through the window after each operation, where available; when open, verify that switch blades have cleared the arc chutes; when closed, verify that the switch blades are inside the arc chutes and vertical; if they are not, perform alignment adjustments per the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Blade alignment | If accessible, verify main blade alignment, penetration, travel stops, and mechanical operation |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Bypass-Isolation Switch (> 1000V) | BISW-MV | 70B-STANDARD | mechanicalServicing
Electrical connections | Check all accessible electrical hardware connections
Operation | Verify operation and alignment of mechanical interlocks
Contact pressure | Verify the contact pressure is within specification using a force gauge or other device that measures forces
Operation | With the door closed and latched, close and open the switch three times to confirm the switch and operator lever is operating; view switch position through the window after each operation, where available; when open, verify that switch blades have cleared the arc chutes; when closed, verify that the switch blades are inside the arc chutes and vertical; if they are not, perform alignment adjustments per the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Disconnect Switch (<= 1000V) | DISC-LV | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
Operation | Perform functional tests for automatic transfer switches, bypass switches, and other transfer switch equipment
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Fused Disconnect Switch (<= 1000V) | DISC-F-LV | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
Operation | Perform functional tests for automatic transfer switches, bypass switches, and other transfer switch equipment
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Transfer Switch (<= 1000V) | MTSW-LV | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
Operation | Perform functional tests for automatic transfer switches, bypass switches, and other transfer switch equipment
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Automatic Transfer Switch (<= 1000V) | ATSW-LV | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
Operation | Perform functional tests for automatic transfer switches, bypass switches, and other transfer switch equipment
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Bolted-Pressure Switch (BPS) | BPSW | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
Operation | Perform functional tests for automatic transfer switches, bypass switches, and other transfer switch equipment
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | High-Pressure Contact Switch (HPC) | HPSW | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
Operation | Perform functional tests for automatic transfer switches, bypass switches, and other transfer switch equipment
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Bypass-Isolation Switch (<= 1000V) | BISW-LV | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
Operation | Perform functional tests for automatic transfer switches, bypass switches, and other transfer switch equipment
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Disconnect Switch (> 1000V) | DISC-MV | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Resistance | Measure the resistance between the line and load terminal pads on each phase
Operation | Verify operation of space heaters, if equipped
Overpotential | Perform overpotential test one pole at a time with the other poles and structure grounded
Overpotential | Perform overpotential test on control wiring | WARNING: Do not perform this test on wiring connected to solid-state components.
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
Operation | Perform functional tests for automatic transfer switches, bypass switches, and other transfer switch equipment
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Fused Disconnect Switch (>1000V) | DISC-F-MV | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Resistance | Measure the resistance between the line and load terminal pads on each phase
Operation | Verify operation of space heaters, if equipped
Overpotential | Perform overpotential test one pole at a time with the other poles and structure grounded
Overpotential | Perform overpotential test on control wiring | WARNING: Do not perform this test on wiring connected to solid-state components.
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
Operation | Perform functional tests for automatic transfer switches, bypass switches, and other transfer switch equipment
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Transfer Switch (> 1000V) | MTSW-MV | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Resistance | Measure the resistance between the line and load terminal pads on each phase
Operation | Verify operation of space heaters, if equipped
Overpotential | Perform overpotential test one pole at a time with the other poles and structure grounded
Overpotential | Perform overpotential test on control wiring | WARNING: Do not perform this test on wiring connected to solid-state components.
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
Operation | Perform functional tests for automatic transfer switches, bypass switches, and other transfer switch equipment
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Automatic Transfer Switch (> 1000V) | ATSW-MV | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Resistance | Measure the resistance between the line and load terminal pads on each phase
Operation | Verify operation of space heaters, if equipped
Overpotential | Perform overpotential test one pole at a time with the other poles and structure grounded
Overpotential | Perform overpotential test on control wiring | WARNING: Do not perform this test on wiring connected to solid-state components.
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
Operation | Perform functional tests for automatic transfer switches, bypass switches, and other transfer switch equipment
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Load-Interruptor Switch | LISW | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Resistance | Measure the resistance between the line and load terminal pads on each phase
Operation | Verify operation of space heaters, if equipped
Overpotential | Perform overpotential test one pole at a time with the other poles and structure grounded
Overpotential | Perform overpotential test on control wiring | WARNING: Do not perform this test on wiring connected to solid-state components.
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
Operation | Perform functional tests for automatic transfer switches, bypass switches, and other transfer switch equipment
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Bypass-Isolation Switch (> 1000V) | BISW-MV | 70B-ENHANCED | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Resistance | Measure the resistance between the line and load terminal pads on each phase
Operation | Verify operation of space heaters, if equipped
Overpotential | Perform overpotential test one pole at a time with the other poles and structure grounded
Overpotential | Perform overpotential test on control wiring | WARNING: Do not perform this test on wiring connected to solid-state components.
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
Operation | Perform functional tests for automatic transfer switches, bypass switches, and other transfer switch equipment
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators | NFPA 70B® Standard De-Energized Electrical Testing Form | Disconnect Switch (<= 1000V) | DISC-LV | 70B-STANDARD | electricalTesting
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators | NFPA 70B® Standard De-Energized Electrical Testing Form | Fused Disconnect Switch (<= 1000V) | DISC-F-LV | 70B-STANDARD | electricalTesting
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators | NFPA 70B® Standard De-Energized Electrical Testing Form | Transfer Switch (<= 1000V) | MTSW-LV | 70B-STANDARD | electricalTesting
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators | NFPA 70B® Standard De-Energized Electrical Testing Form | Automatic Transfer Switch (<= 1000V) | ATSW-LV | 70B-STANDARD | electricalTesting
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators | NFPA 70B® Standard De-Energized Electrical Testing Form | Bolted-Pressure Switch (BPS) | BPSW | 70B-STANDARD | electricalTesting
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators | NFPA 70B® Standard De-Energized Electrical Testing Form | High-Pressure Contact Switch (HPC) | HPSW | 70B-STANDARD | electricalTesting
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators | NFPA 70B® Standard De-Energized Electrical Testing Form | Bypass-Isolation Switch (<= 1000V) | BISW-LV | 70B-STANDARD | electricalTesting
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Disconnect Switch (> 1000V) | DISC-MV | 70B-STANDARD | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Resistance | Measure the resistance between the line and load terminal pads on each phase
Operation | Verify operation of space heaters, if equipped
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Fused Disconnect Switch (>1000V) | DISC-F-MV | 70B-STANDARD | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Resistance | Measure the resistance between the line and load terminal pads on each phase
Operation | Verify operation of space heaters, if equipped
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Transfer Switch (> 1000V) | MTSW-MV | 70B-STANDARD | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Resistance | Measure the resistance between the line and load terminal pads on each phase
Operation | Verify operation of space heaters, if equipped
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Automatic Transfer Switch (> 1000V) | ATSW-MV | 70B-STANDARD | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Resistance | Measure the resistance between the line and load terminal pads on each phase
Operation | Verify operation of space heaters, if equipped
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Load-Interruptor Switch | LISW | 70B-STANDARD | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Resistance | Measure the resistance between the line and load terminal pads on each phase
Operation | Verify operation of space heaters, if equipped
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Measure contact resistance of each switching pole |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Bypass-Isolation Switch (> 1000V) | BISW-MV | 70B-STANDARD | electricalTesting
Insulation resistance | Perform insulation-resistance tests, phase-to-phase and phase-to-ground with switch closed and across each open pole
Control power | Verify control power for close and trip functions* | *Only for switches with motor operators
Operation | Verify the electrical operation of switch* | *Only for switches with motor operators
Trip | Perform trip and close tests* | *Only for switches with motor operators
Operation | Verify operation of the switch from local switches or terminal blocks* | *Only for switches with motor operators
Operation | Functional tests only for switches with shunt trip capabilities
Resistance | Measure the resistance between the line and load terminal pads on each phase
Operation | Verify operation of space heaters, if equipped
Arc reduction technology | Test arc reduction technology in accordance with the manufacturer’s instructions

## ch.18
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Physical condition, including operating environment | Damage or deterioration, supports or restraints, bending radius, excessive tension, signs of overheating, corrosion, swelling or soft spots | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Power Cable / Conductor (<= 1000V) | CABL-LV | 70B-ENHANCED | visualInspection
Labeling | Correct labeling or identification | Phasing, cable ID, multiple sources, hazard, other warning labels
Grounding and bonding | Grounding/bonding | Damage, missing or loose terminations, clearance from energized parts, protection from physical damage
Vaults | Vaults containing cables | Damage, concrete deterioration, drainage
Terminations | Cable and conductor terminations | Oil or compound leaks, cracks or damaged bodies, cleanliness, terminations
Aerial installation | Aerial installations | Damage, deteriorating supports, suspension systems, pinched or damaged insulation at dead ends, animal or bird infestation
Raceway | Raceway | Damage or deterioration, abrasion or wear, continuity, tight joints, missing or loose bonding jumpers, corrosion
Barriers | Barriers, guards, and assemblies | Damage or signs of deterioration, arcing, tracking, supports and mounting hardware
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Physical condition, including operating environment | Damage or deterioration, supports or restraints, bending radius, excessive tension, signs of overheating, corrosion, swelling or soft spots | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Power Cable / Conductor (> 1000V) | CABL-MV | 70B-ENHANCED | visualInspection
Labeling | Correct labeling or identification | Phasing, cable ID, multiple sources, hazard, other warning labels
Grounding and bonding | Grounding/bonding | Damage, missing or loose terminations, clearance from energized parts, protection from physical damage
Vaults | Vaults containing cables | Damage, concrete deterioration, drainage
Terminations | Cable and conductor terminations | Oil or compound leaks, cracks or damaged bodies, cleanliness, terminations
Aerial installation | Aerial installations | Damage, deteriorating supports, suspension systems, pinched or damaged insulation at dead ends, animal or bird infestation
Raceway | Raceway | Damage or deterioration, abrasion or wear, continuity, tight joints, missing or loose bonding jumpers, corrosion
Barriers | Barriers, guards, and assemblies | Damage or signs of deterioration, arcing, tracking, supports and mounting hardware
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Physical condition, including operating environment | Damage or deterioration, supports or restraints, bending radius, excessive tension, signs of overheating, corrosion, swelling or soft spots | NFPA 70B® Standard De-Energized Visual Inspection Form | Power Cable / Conductor (<= 1000V) | CABL-LV | 70B-STANDARD | visualInspection
Labeling | Correct labeling or identification | Phasing, cable ID, multiple sources, hazard, other warning labels
Grounding and bonding | Grounding/bonding | Damage, missing or loose terminations, clearance from energized parts, protection from physical damage
Vaults | Vaults containing cables | Damage, concrete deterioration, drainage
Terminations | Cable and conductor terminations | Oil or compound leaks, cracks or damaged bodies, cleanliness, terminations
Aerial installation | Aerial installations | Damage, deteriorating supports, suspension systems, pinched or damaged insulation at dead ends, animal or bird infestation
Raceway | Raceway | Damage or deterioration, abrasion or wear, continuity, tight joints, missing or loose bonding jumpers, corrosion
Barriers | Barriers, guards, and assemblies | Damage or signs of deterioration, arcing, tracking, supports and mounting hardware
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Physical condition, including operating environment | Damage or deterioration, supports or restraints, bending radius, excessive tension, signs of overheating, corrosion, swelling or soft spots | NFPA 70B® Standard De-Energized Visual Inspection Form | Power Cable / Conductor (> 1000V) | CABL-MV | 70B-STANDARD | visualInspection
Labeling | Correct labeling or identification | Phasing, cable ID, multiple sources, hazard, other warning labels
Grounding and bonding | Grounding/bonding | Damage, missing or loose terminations, clearance from energized parts, protection from physical damage
Vaults | Vaults containing cables | Damage, concrete deterioration, drainage
Terminations | Cable and conductor terminations | Oil or compound leaks, cracks or damaged bodies, cleanliness, terminations
Aerial installation | Aerial installations | Damage, deteriorating supports, suspension systems, pinched or damaged insulation at dead ends, animal or bird infestation
Raceway | Raceway | Damage or deterioration, abrasion or wear, continuity, tight joints, missing or loose bonding jumpers, corrosion
Barriers | Barriers, guards, and assemblies | Damage or signs of deterioration, arcing, tracking, supports and mounting hardware
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Physical condition, including operating environment | Damage or deterioration, supports or restraints, bending radius, excessive tension, signs of overheating, corrosion, swelling or soft spots | Basic Energized Visual Inspection Form | Power Cable / Conductor (<= 1000V) | CABL-LV | BASIC | visualInspection
Labeling | Correct labeling or identification | Phasing, cable ID, multiple sources, hazard, other warning labels
Grounding and bonding | Grounding/bonding | Damage, missing or loose terminations, clearance from energized parts, protection from physical damage
Vaults | Vaults containing cables | Damage, concrete deterioration, drainage
Terminations | Cable and conductor terminations | Oil or compound leaks, cracks or damaged bodies, cleanliness, terminations
Aerial installation | Aerial installations | Damage, deteriorating supports, suspension systems, pinched or damaged insulation at dead ends, animal or bird infestation
Raceway | Raceway | Damage or deterioration, abrasion or wear, continuity, tight joints, missing or loose bonding jumpers, corrosion
Barriers | Barriers, guards, and assemblies | Damage or signs of deterioration, arcing, tracking, supports and mounting hardware
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Physical condition, including operating environment | Damage or deterioration, supports or restraints, bending radius, excessive tension, signs of overheating, corrosion, swelling or soft spots | Basic Energized Visual Inspection Form | Power Cable / Conductor (> 1000V) | CABL-MV | BASIC | visualInspection
Labeling | Correct labeling or identification | Phasing, cable ID, multiple sources, hazard, other warning labels
Grounding and bonding | Grounding/bonding | Damage, missing or loose terminations, clearance from energized parts, protection from physical damage
Vaults | Vaults containing cables | Damage, concrete deterioration, drainage
Terminations | Cable and conductor terminations | Oil or compound leaks, cracks or damaged bodies, cleanliness, terminations
Aerial installation | Aerial installations | Damage, deteriorating supports, suspension systems, pinched or damaged insulation at dead ends, animal or bird infestation
Raceway | Raceway | Damage or deterioration, abrasion or wear, continuity, tight joints, missing or loose bonding jumpers, corrosion
Barriers | Barriers, guards, and assemblies | Damage or signs of deterioration, arcing, tracking, supports and mounting hardware
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Cable and conductor insulation, jackets, sheaths, terminals or terminations, enclosures, and insulating materials shall be kept clean to prevent a buildup of contaminants that can negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Power Cable / Conductor (<= 1000V) | CABL-LV | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Cable and conductor insulation, jackets, sheaths, terminals or terminations, enclosures, and insulating materials shall be kept clean to prevent a buildup of contaminants that can negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Power Cable / Conductor (> 1000V) | CABL-MV | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Cable and conductor insulation, jackets, sheaths, terminals or terminations, enclosures, and insulating materials shall be kept clean to prevent a buildup of contaminants that can negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Standard De-Energized Cleaning Form | Power Cable / Conductor (<= 1000V) | CABL-LV | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Cable and conductor insulation, jackets, sheaths, terminals or terminations, enclosures, and insulating materials shall be kept clean to prevent a buildup of contaminants that can negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Standard De-Energized Cleaning Form | Power Cable / Conductor (> 1000V) | CABL-MV | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Terminating devices, elbows, or T-bodies shall be lubricated in accordance with the manufacturer’s instructions. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Power Cable / Conductor (<= 1000V) | CABL-LV | 70B-ENHANCED | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Terminating devices, elbows, or T-bodies shall be lubricated in accordance with the manufacturer’s instructions. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Power Cable / Conductor (> 1000V) | CABL-MV | 70B-ENHANCED | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Terminating devices, elbows, or T-bodies shall be lubricated in accordance with the manufacturer’s instructions. |  | NFPA 70B® Standard De-Energized Lubrication Form | Power Cable / Conductor (<= 1000V) | CABL-LV | 70B-STANDARD | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Terminating devices, elbows, or T-bodies shall be lubricated in accordance with the manufacturer’s instructions. |  | NFPA 70B® Standard De-Energized Lubrication Form | Power Cable / Conductor (> 1000V) | CABL-MV | 70B-STANDARD | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Insulation resistance | Insulation resistance |  | NFPA 70B® Enhanced De-Energized* Electrical Testing Form | Power Cable / Conductor (<= 1000V) | CABL-LV | 70B-ENHANCED | electricalTesting
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ultrasonic | Airborne ultrasonic acoustic emissions* | *test conducted energized | NFPA 70B® Enhanced De-Energized* Electrical Testing Form | Power Cable / Conductor (> 1000V) | CABL-MV | 70B-ENHANCED | electricalTesting
VLF | Very low frequency (VLF <1 Hz)
Overpotential | Overpotential test (hi-pot)
Tan Delta | Dissipation factor/tan delta
Partial discharge | Partial discharge* | *test conducted energized
Power frequency | Power frequency
Oscillating wave | Oscillating wave
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
VLF | Very low frequency (VLF <1 Hz) |  | NFPA 70B® Standard De-Energized* Electrical Testing Form | Power Cable / Conductor (> 1000V) | CABL-MV | 70B-STANDARD | electricalTesting
Overpotential | Overpotential test (hi-pot)
Tan Delta | Dissipation factor/tan delta
Partial discharge | Partial discharge* | *test conducted energized
Power frequency | Power frequency
Oscillating wave | Oscillating wave

## ch.19
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Grounding and bonding | Verify equipment grounding and bonding for cable tray |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Cable Tray System | CBLT | 70B-ENHANCED | visualInspection
Grounding and bonding | Verify equipment grounding and bonding for transition raceways
Overfilling | Check for overfilling
Cables | Inspect for incorrect cables (small, not TC listed)
Cables | Inspect for cable damage
Cables | Inspect for cables support damage
Obstruction | Inspect for intrusive items (e.g., pipes, hangers)
Cables | Inspect spacing of cables, for cables that have minimum spacing requirements
Cables | Inspect cable tie-downs
Cables | Inspect supports of cable trays
Supports | Inspect for damaged tray or supports
Joints | Verify expansion joints in sufficient distances
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Grounding and bonding | Verify equipment grounding and bonding for cable tray |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Cable Tray System | CBLT | 70B-STANDARD | visualInspection
Grounding and bonding | Verify equipment grounding and bonding for transition raceways
Overfilling | Check for overfilling
Cables | Inspect for cables support damage
Obstruction | Inspect for intrusive items (e.g., pipes, hangers)
Cables | Inspect spacing of cables, for cables that have minimum spacing requirements
Cables | Inspect cable tie-downs
Cables | Inspect supports of cable trays
Supports | Inspect for damaged tray or supports
Joints | Verify expansion joints in sufficient distances
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Grounding and bonding | Verify equipment grounding and bonding for cable tray |  | Basic Energized Visual Inspection Form | Cable Tray System | CBLT | BASIC | visualInspection
Grounding and bonding | Verify equipment grounding and bonding for transition raceways
Overfilling | Check for overfilling
Cables | Inspect for cables support damage
Obstruction | Inspect for intrusive items (e.g., pipes, hangers)
Cables | Inspect spacing of cables, for cables that have minimum spacing requirements
Cables | Inspect cable tie-downs
Cables | Inspect supports of cable trays
Supports | Inspect for damaged tray or supports
Joints | Verify expansion joints in sufficient distances
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Cable trays and the cables within shall be kept clean to prevent a buildup of contaminants that can negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Cable Tray System | CBLT | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Cable trays and the cables within shall be kept clean to prevent a buildup of contaminants that can negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Standard De-Energized Cleaning Form | Cable Tray System | CBLT | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ground fault current | Test cable tray effective ground fault current path for continuity |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Cable Tray System | CBLT | 70B-ENHANCED | electricalTesting

## ch.20
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Condition | Inspect physical and mechanical condition of accessible and visible components and connections |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Grounding | GRND | 70B-ENHANCED | visualInspection
Anchorage | Inspect anchorage
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Condition | Inspect physical and mechanical condition of accessible and visible components and connections |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Bonding | BNDG | 70B-ENHANCED | visualInspection
Anchorage | Inspect anchorage
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Condition | Inspect physical and mechanical condition of accessible and visible components and connections |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Grounding | GRND | 70B-STANDARD | visualInspection
Anchorage | Inspect anchorage
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Condition | Inspect physical and mechanical condition of accessible and visible components and connections |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Bonding | BNDG | 70B-STANDARD | visualInspection
Anchorage | Inspect anchorage
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Measure bolted or mechanical connection resistance |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Grounding | GRND | 70B-ENHANCED | electricalTesting
Ground rod system | For ground rod electrode systems, perform fall-of-potential test to measure grounding rod to earth resistance
PPGR | Perform point-to-point test to verify equipment is bonded together
SSGR | Perform substation grounding electrode system and substation grid integrity test by injecting current in accordance with industry practices
Voltage | Measure voltage between the equipment grounding conductor and the grounded conductor* | *test conducted energized
Current | Measure current magnitude on the equipment grounding conductor* | *test conducted energized
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Measure bolted or mechanical connection resistance |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Bonding | BNDG | 70B-ENHANCED | electricalTesting
Ground rod system | For ground rod electrode systems, perform fall-of-potential test to measure grounding rod to earth resistance
PPGR | Perform point-to-point test to verify equipment is bonded together
SSGR | Perform substation grounding electrode system and substation grid integrity test by injecting current in accordance with industry practices
Voltage | Measure voltage between the equipment grounding conductor and the grounded conductor* | *test conducted energized
Current | Measure current magnitude on the equipment grounding conductor* | *test conducted energized

## ch.21
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Connection | Verify ground connection is made on the source side of the neutral disconnect link and any ground fault sensors |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Low-Voltage Integral Ground Fault Protection System | GFPS-I-LV | 70B-ENHANCED | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Connection | Verify ground connection is made on the source side of the neutral disconnect link and any ground fault sensors |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Low-Voltage External Ground Fault Protection System | GFPS-E-LV | 70B-ENHANCED | visualInspection
Conductors | For zero-sequence systems, verify all phase and neutral conductors pass through the sensor in the same direction, and that grounding conductors do not pass through the sensor
Components | Verify sensor, wiring, and ground-fault components are not damaged
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Connection | Verify ground connection is made on the source side of the neutral disconnect link and any ground fault sensors |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Medium-Voltage Integral Ground Fault Protection System | GFPS-I-MV | 70B-ENHANCED | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Connection | Verify ground connection is made on the source side of the neutral disconnect link and any ground fault sensors |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Medium-Voltage External Groudn Fault Protection System | GFPS-E-MV | 70B-ENHANCED | visualInspection
Conductors | For zero-sequence systems, verify all phase and neutral conductors pass through the sensor in the same direction, and that grounding conductors do not pass through the sensor
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Connection | Verify ground connection is made on the source side of the neutral disconnect link and any ground fault sensors |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Low-Voltage Integral Ground Fault Protection System | GFPS-I-LV | 70B-STANDARD | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Connection | Verify ground connection is made on the source side of the neutral disconnect link and any ground fault sensors |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Low-Voltage External Ground Fault Protection System | GFPS-E-LV | 70B-STANDARD | visualInspection
Conductors | For zero-sequence systems, verify all phase and neutral conductors pass through the sensor in the same direction, and that grounding conductors do not pass through the sensor
Components | Verify sensor, wiring, and ground-fault components are not damaged
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Connection | Verify ground connection is made on the source side of the neutral disconnect link and any ground fault sensors |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Medium-Voltage Integral Ground Fault Protection System | GFPS-I-MV | 70B-STANDARD | visualInspection
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Connection | Verify ground connection is made on the source side of the neutral disconnect link and any ground fault sensors |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Medium-Voltage External Groudn Fault Protection System | GFPS-E-MV | 70B-STANDARD | visualInspection
Conductors | For zero-sequence systems, verify all phase and neutral conductors pass through the sensor in the same direction, and that grounding conductors do not pass through the sensor
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the relay case and cover |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Low-Voltage External Ground Fault Protection System | GFPS-E-LV | 70B-ENHANCED | cleaning
Cleanliness | Clean sensors and associated ground-fault protection system components
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean sensors and associated ground-fault protection system components |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Medium-Voltage External Groudn Fault Protection System | GFPS-E-MV | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the relay case and cover |  | NFPA 70B® Standard De-Energized Cleaning Form | Low-Voltage External Ground Fault Protection System | GFPS-E-LV | 70B-STANDARD | cleaning
Cleanliness | Clean sensors and associated ground-fault protection system components
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean sensors and associated ground-fault protection system components |  | NFPA 70B® Standard De-Energized Cleaning Form | Medium-Voltage External Groudn Fault Protection System | GFPS-E-MV | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Operation | Verify correct operation of the self-test panel/trip unit functions |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Low-Voltage Integral Ground Fault Protection System | GFPS-I-LV | 70B-ENHANCED | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Inspect bolted electrical connections |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Medium-Voltage External Groudn Fault Protection System | GFPS-E-LV | 70B-ENHANCED | mechanicalServicing
Operation | Verify correct operation of the self-test panel/trip unit functions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Operation | Verify correct operation of the self-test panel/trip unit functions |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Low-Voltage External Ground Fault Protection System | GFPS-I-MV | 70B-ENHANCED | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Inspect bolted electrical connections |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Medium-Voltage External Groudn Fault Protection System | GFPS-E-MV | 70B-ENHANCED | mechanicalServicing
Operation | Verify correct operation of the self-test panel/trip unit functions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Operation | Verify correct operation of the self-test panel/trip unit functions |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Low-Voltage Integral Ground Fault Protection System | GFPS-I-LV | 70B-STANDARD | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Inspect bolted electrical connections |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Medium-Voltage External Groudn Fault Protection System | GFPS-E-LV | 70B-STANDARD | mechanicalServicing
Operation | Verify correct operation of the self-test panel/trip unit functions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Operation | Verify correct operation of the self-test panel/trip unit functions |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Low-Voltage External Ground Fault Protection System | GFPS-I-MV | 70B-STANDARD | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Inspect bolted electrical connections |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Medium-Voltage External Groudn Fault Protection System | GFPS-E-MV | 70B-STANDARD | mechanicalServicing
Operation | Verify correct operation of the self-test panel/trip unit functions
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Resistance | Measure system neutral-to-ground resistance with the neutral disconnect link removed, and verify no downstream grounds exist on the neutral |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Low-Voltage Integral Ground Fault Protection System | GFPS-I-LV | 70B-ENHANCED | electricalTesting
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Resistance | Measure system neutral-to-ground resistance with the neutral disconnect link removed, and verify no downstream grounds exist on the neutral |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Medium-Voltage External Groudn Fault Protection System | GFPS-E-LV | 70B-ENHANCED | electricalTesting
Trip | Verify reduced control voltage tripping ability at 55% for ac systems and 80% for dc systems
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Resistance | Measure system neutral-to-ground resistance with the neutral disconnect link removed, and verify no downstream grounds exist on the neutral |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Low-Voltage Integral Ground Fault Protection System | GFPS-I-LV | 70B-STANDARD | electricalTesting
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Resistance | Measure system neutral-to-ground resistance with the neutral disconnect link removed, and verify no downstream grounds exist on the neutral |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Medium-Voltage External Groudn Fault Protection System | GFPS-E-LV | 70B-STANDARD | electricalTesting

## ch.25
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Static UPS System | UPSS | 70B-ENHANCED | visualInspection
Fans | Check fans for operation
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition including corrosion
Capacitors | Inspect capacitors for swelling and discoloration
Currenty-carrying parts | Check visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Recitifer and inverter | Inspect rectifier and inverter assembly | Inspect for signs of overheating or deterioration.
Static switch | Inspect static switch module | Inspect for signs of overheating or deterioration.
Interface | Inspect interface, control, I/O boards, and dc capacitor boards | Inspect for signs of overheating or deterioration.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Rotary UPS System | UPSR | 70B-ENHANCED | visualInspection
Fans | Check fans for operation
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition including corrosion
Current-carrying parts | Check visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Interface | Inspect interface, control, I/O boards, and dc capacitor boards | Inspect for signs of overheating or deterioration.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Hybrid UPS System | UPSH | 70B-ENHANCED | visualInspection
Fans | Check fans for operation
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition including corrosion
Capacitors | Inspect capacitors for swelling and discoloration
Currenty-carrying parts | Check visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Recitifer and inverter | Inspect rectifier and inverter assembly | Inspect for signs of overheating or deterioration.
Static switch | Inspect static switch module | Inspect for signs of overheating or deterioration.
Interface | Inspect interface, control, I/O boards, and dc capacitor boards | Inspect for signs of overheating or deterioration.
For individual components, refer to the appropriate chapter(s) of this standard
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Static UPS System | UPSS | 70B-STANDARD | visualInspection
Fans | Check fans for operation
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition including corrosion
Capacitors | Inspect capacitors for swelling and discoloration
Currenty-carrying parts | Check visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Recitifer and inverter | Inspect rectifier and inverter assembly | Inspect for signs of overheating or deterioration.
Static switch | Inspect static switch module | Inspect for signs of overheating or deterioration.
Interface | Inspect interface, control, I/O boards, and dc capacitor boards | Inspect for signs of overheating or deterioration.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Rotary UPS System | UPSR | 70B-STANDARD | visualInspection
Fans | Check fans for operation
Wiring | Inspect wiring, bus, cables, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition including corrosion
Current-carrying parts | Check visible current-carrying parts and control devices, if applicable, for signs of overheating or deterioration
Interface | Inspect interface, control, I/O boards, and dc capacitor boards | Inspect for signs of overheating or deterioration.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Hybrid UPS System | UPSH | 70B-STANDARD | visualInspection
Fans | Check fans for operation
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | Basic Energized Visual Inspection Form | Static UPS System | UPSS | BASIC | visualInspection
Fans | Check fans for operation
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | Basic Energized Visual Inspection Form | Rotary UPS System | UPSR | BASIC | visualInspection
Fans | Check fans for operation
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Physical condition | Inspect doors and latches for fit, dents, corrosion, and missing hardware |  | Basic Energized Visual Inspection Form | Hybrid UPS System | UPSH | BASIC | visualInspection
Fans | Check fans for operation
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Replace the air filters and verify the vents are clear |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Static UPS System | UPSS | 70B-ENHANCED | cleaning
Cleanliness | Vacuum enclosure
Cleanliness | Clean exposed switch contacts with a multipurpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
Cleanliness | Wipe contact surfaces with a noncorrosive cleaning agent
Cleanliness | Clean insulators
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Replace the air filters and verify the vents are clear |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Rotary UPS System | UPSR | 70B-ENHANCED | cleaning
Cleanliness | Vacuum enclosure
Cleanliness | Clean exposed switch contacts with a multipurpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
Cleanliness | Wipe contact surfaces with a noncorrosive cleaning agent
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Replace the air filters and verify the vents are clear |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Hybrid UPS System | UPSH | 70B-ENHANCED | cleaning
Cleanliness | Vacuum enclosure
Cleanliness | Clean exposed switch contacts with a multipurpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
Cleanliness | Wipe contact surfaces with a noncorrosive cleaning agent
Cleanliness | Clean insulators
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Replace the air filters and verify the vents are clear |  | NFPA 70B® Standard De-Energized Cleaning Form | Static UPS System | UPSS | 70B-STANDARD | cleaning
Cleanliness | Vacuum enclosure
Cleanliness | Clean exposed switch contacts with a multipurpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
Cleanliness | Wipe contact surfaces with a noncorrosive cleaning agent
Cleanliness | Clean insulators
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Replace the air filters and verify the vents are clear |  | NFPA 70B® Standard De-Energized Cleaning Form | Rotary UPS System | UPSR | 70B-STANDARD | cleaning
Cleanliness | Vacuum enclosure
Cleanliness | Clean exposed switch contacts with a multipurpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
Cleanliness | Wipe contact surfaces with a noncorrosive cleaning agent
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Replace the air filters and verify the vents are clear |  | NFPA 70B® Standard De-Energized Cleaning Form | Hybrid UPS System | UPSH | 70B-STANDARD | cleaning
Cleanliness | Vacuum enclosure
Cleanliness | Clean exposed switch contacts with a multipurpose precision lubricant before lubricating
Cleanliness | Wipe contact surfaces with a lint-free cleaning cloth
Cleanliness | Wipe contact surfaces with a noncorrosive cleaning agent
Cleanliness | Clean insulators
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Lubricate rotating equipment |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Rotary UPS System | UPSR | 70B-ENHANCED | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Lubricate rotating equipment |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Hybrid UPS System | UPSH | 70B-ENHANCED | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Lubricate rotating equipment |  | NFPA 70B® Standard De-Energized Lubrication Form | Rotary UPS System | UPSR | 70B-STANDARD | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Lubricate rotating equipment |  | NFPA 70B® Standard De-Energized Lubrication Form | Hybrid UPS System | UPSH | 70B-STANDARD | lubrication
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Interlocks | Verify operation and alignment of mechanical safety interlocks |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Static UPS System | UPSS | 70B-ENHANCED | mechanicalServicing
Electrical connections | Check electrical hardware connections
Breakers | Perform mechanical servicing for system circuit breakers
Transfer systems | Transfer systems
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Interlocks | Verify operation and alignment of mechanical safety interlocks |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Rotary UPS System | UPSR | 70B-ENHANCED | mechanicalServicing
Electrical connections | Check electrical hardware connections
Breakers | Perform mechanical servicing for system circuit breakers
Transfer systems | Transfer systems
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Interlocks | Verify operation and alignment of mechanical safety interlocks |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Hybrid UPS System | UPSH | 70B-ENHANCED | mechanicalServicing
Electrical connections | Check electrical hardware connections
Breakers | Perform mechanical servicing for system circuit breakers
Transfer systems | Transfer systems
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Interlocks | Verify operation and alignment of mechanical safety interlocks |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Static UPS System | UPSS | 70B-STANDARD | mechanicalServicing
Electrical connections | Check electrical hardware connections
Breakers | Perform mechanical servicing for system circuit breakers
Transfer systems | Transfer systems
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Interlocks | Verify operation and alignment of mechanical safety interlocks |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Rotary UPS System | UPSR | 70B-STANDARD | mechanicalServicing
Electrical connections | Check electrical hardware connections
Breakers | Perform mechanical servicing for system circuit breakers
Transfer systems | Transfer systems
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Interlocks | Verify operation and alignment of mechanical safety interlocks |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Hybrid UPS System | UPSH | 70B-STANDARD | mechanicalServicing
Electrical connections | Check electrical hardware connections
Breakers | Perform mechanical servicing for system circuit breakers
Transfer systems | Transfer systems
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Neutral output current | Measure the neutral output current during peak loads* | *test performed energized. Conduct every 3 months or when new equipment is added to the system | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Static UPS System | UPSS | 70B-ENHANCED | electricalTesting
Operating parameters | Record all operating parameters, such as frequency, voltage, and current, at the bypass switch, input, output, batteries, and modules, where applicable | *test performed energized.
Static transfer | Test static transfer from normal to bypass and back to normal
Interlock | Electrical interlock systems, alarms, and indicator circuits
Alarms | Perform operational test on all alarms and emergency shutdowns, where applicable
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Neutral output current | Measure the neutral output current during peak loads* | *test performed energized. Conduct every 3 months or when new equipment is added to the system | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Rotary UPS System | UPSR | 70B-ENHANCED | electricalTesting
Operating parameters | Record all operating parameters, such as frequency, voltage, and current, at the bypass switch, input, output, batteries, and modules, where applicable | *test performed energized.
Static transfer | Test static transfer from normal to bypass and back to normal
Interlock | Electrical interlock systems, alarms, and indicator circuits
Alarms | Perform operational test on all alarms and emergency shutdowns, where applicable
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Neutral output current | Measure the neutral output current during peak loads* | *test performed energized. Conduct every 3 months or when new equipment is added to the system | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Hybrid UPS System | UPSH | 70B-ENHANCED | electricalTesting
Operating parameters | Record all operating parameters, such as frequency, voltage, and current, at the bypass switch, input, output, batteries, and modules, where applicable | *test performed energized.
Static transfer | Test static transfer from normal to bypass and back to normal
Interlock | Electrical interlock systems, alarms, and indicator circuits
Alarms | Perform operational test on all alarms and emergency shutdowns, where applicable
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Operating parameters | Record all operating parameters, such as frequency, voltage, and current, at the bypass switch, input, output, batteries, and modules, where applicable | *test performed energized. Conduct every 3 months or when new equipment is added to the system | NFPA 70B® Standard De-Energized Electrical Testing Form | Static UPS System | UPSS | 70B-STANDARD | electricalTesting
Static transfer | Test static transfer from normal to bypass and back to normal | *test performed energized.
Interlock | Electrical interlock systems, alarms, and indicator circuits
Alarms | Perform operational test on all alarms and emergency shutdowns, where applicable
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Operating parameters | Record all operating parameters, such as frequency, voltage, and current, at the bypass switch, input, output, batteries, and modules, where applicable | *test performed energized. Conduct every 3 months or when new equipment is added to the system | NFPA 70B® Standard De-Energized Electrical Testing Form | Rotary UPS System | UPSR | 70B-STANDARD | electricalTesting
Static transfer | Test static transfer from normal to bypass and back to normal | *test performed energized.
Interlock | Electrical interlock systems, alarms, and indicator circuits
Alarms | Perform operational test on all alarms and emergency shutdowns, where applicable
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Operating parameters | Record all operating parameters, such as frequency, voltage, and current, at the bypass switch, input, output, batteries, and modules, where applicable | *test performed energized. Conduct every 3 months or when new equipment is added to the system | NFPA 70B® Standard De-Energized Electrical Testing Form | Hybrid UPS System | UPSH | 70B-STANDARD | electricalTesting
Static transfer | Test static transfer from normal to bypass and back to normal | *test performed energized.
Interlock | Electrical interlock systems, alarms, and indicator circuits
Alarms | Perform operational test on all alarms and emergency shutdowns, where applicable
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Operating parameters | Record all operating parameters, such as frequency, voltage, and current, at the bypass switch, input, output, batteries, and modules, where applicable |  | Basic Energized Electrical Testing Form | Static UPS System | UPSS | BASIC | electricalTesting
Static transfer | Test static transfer from normal to bypass and back to normal
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Operating parameters | Record all operating parameters, such as frequency, voltage, and current, at the bypass switch, input, output, batteries, and modules, where applicable |  | Basic Energized Electrical Testing Form | Rotary UPS System | UPSR | BASIC | electricalTesting
Static transfer | Test static transfer from normal to bypass and back to normal
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Operating parameters | Record all operating parameters, such as frequency, voltage, and current, at the bypass switch, input, output, batteries, and modules, where applicable |  | Basic Energized Electrical Testing Form | Hybrid UPS System | UPSH | BASIC | electricalTesting
Static transfer | Test static transfer from normal to bypass and back to normal
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Operating parameters | Equipment software upgrades and revisions shall be performed as needed. |  | NFPA 70B® Enhanced De-Energized Special Testing Form | Static UPS System | UPSS | 70B-ENHANCED | specialTesting
Static transfer | Load Transfer and Load Testing | see NFPA 70B 25.4.2
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Operating parameters | Equipment software upgrades and revisions shall be performed as needed. |  | NFPA 70B® Enhanced De-Energized Special Testing Form | Rotary UPS System | UPSR | 70B-ENHANCED | specialTesting
Static transfer | Load Transfer and Load Testing | see NFPA 70B 25.4.2
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Operating parameters | Equipment software upgrades and revisions shall be performed as needed. |  | NFPA 70B® Enhanced De-Energized Special Testing Form | Hybrid UPS System | UPSH | 70B-ENHANCED | specialTesting
Static transfer | Load Transfer and Load Testing | see NFPA 70B 25.4.2
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Operating parameters | Equipment software upgrades and revisions shall be performed as needed. |  | NFPA 70B® Standard De-Energized Special Testing Form | Static UPS System | UPSS | 70B-STANDARD | specialTesting
Static transfer | Load Transfer and Load Testing | see NFPA 70B 25.4.2
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Operating parameters | Equipment software upgrades and revisions shall be performed as needed. |  | NFPA 70B® Standard De-Energized Special Testing Form | Rotary UPS System | UPSR | 70B-STANDARD | specialTesting
Static transfer | Load Transfer and Load Testing | see NFPA 70B 25.4.2
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Operating parameters | Equipment software upgrades and revisions shall be performed as needed. |  | NFPA 70B® Standard De-Energized Special Testing Form | Hybrid UPS System | UPSH | 70B-STANDARD | specialTesting
Static transfer | Load Transfer and Load Testing | see NFPA 70B 25.4.2

## ch.27
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Application | Application | Ensure the machinery is installed in accordance with the manufacturer’s listing and labeling and applicable codes/standards. | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Low-Voltage Machine (<= 200hp) | LVMT-S | 70B-ENHANCED | visualInspection
Physical condition | Physical condition
Indicating device status | Indicating device status
Labeling | Labeling
Grounding/bonding | Grounding/bonding
Machinery alignment | Machinery alignment | Intended where signs of misalignment exist.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Application | Application | Ensure the machinery is installed in accordance with the manufacturer’s listing and labeling and applicable codes/standards. | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Low-Voltage Machine (>200hp) | LVMT-L | 70B-ENHANCED | visualInspection
Physical condition | Physical condition
Indicating device status | Indicating device status
Labeling | Labeling
Grounding/bonding | Grounding/bonding
Machinery alignment | Machinery alignment | Intended where signs of misalignment exist.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Application | Application | Ensure the machinery is installed in accordance with the manufacturer’s listing and labeling and applicable codes/standards. | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Low-Voltage Machine (dc) | LVMT-DC | 70B-ENHANCED | visualInspection
Physical condition | Physical condition
Indicating device status | Indicating device status
Labeling | Labeling
Grounding/bonding | Grounding/bonding
Machinery alignment | Machinery alignment | Intended where signs of misalignment exist.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Application | Application | Ensure the machinery is installed in accordance with the manufacturer’s listing and labeling and applicable codes/standards. | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Medium-Voltage Induction Machine | MVIN | 70B-ENHANCED | visualInspection
Physical condition | Physical condition
Indicating device status | Indicating device status
Labeling | Labeling
Grounding/bonding | Grounding/bonding
Machinery alignment | Machinery alignment | Intended where signs of misalignment exist.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Application | Application | Ensure the machinery is installed in accordance with the manufacturer’s listing and labeling and applicable codes/standards. | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Medium-Voltage Synchronous Machine | MVSC | 70B-ENHANCED | visualInspection
Physical condition | Physical condition
Indicating device status | Indicating device status
Labeling | Labeling
Grounding/bonding | Grounding/bonding
Machinery alignment | Machinery alignment | Intended where signs of misalignment exist.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Application | Application | Ensure the machinery is installed in accordance with the manufacturer’s listing and labeling and applicable codes/standards. | NFPA 70B® Standard De-Energized Visual Inspection Form | Low-Voltage Machine (<= 200hp) | LVMT-S | 70B-STANDARD | visualInspection
Physical condition | Physical condition
Indicating device status | Indicating device status
Labeling | Labeling
Grounding/bonding | Grounding/bonding
Machinery alignment | Machinery alignment | Intended where signs of misalignment exist.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Application | Application | Ensure the machinery is installed in accordance with the manufacturer’s listing and labeling and applicable codes/standards. | NFPA 70B® Standard De-Energized Visual Inspection Form | Low-Voltage Machine (>200hp) | LVMT-L | 70B-STANDARD | visualInspection
Physical condition | Physical condition
Indicating device status | Indicating device status
Labeling | Labeling
Grounding/bonding | Grounding/bonding
Machinery alignment | Machinery alignment | Intended where signs of misalignment exist.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Application | Application | Ensure the machinery is installed in accordance with the manufacturer’s listing and labeling and applicable codes/standards. | NFPA 70B® Standard De-Energized Visual Inspection Form | Low-Voltage Machine (dc) | LVMT-DC | 70B-STANDARD | visualInspection
Physical condition | Physical condition
Indicating device status | Indicating device status
Labeling | Labeling
Grounding/bonding | Grounding/bonding
Machinery alignment | Machinery alignment | Intended where signs of misalignment exist.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Application | Application | Ensure the machinery is installed in accordance with the manufacturer’s listing and labeling and applicable codes/standards. | NFPA 70B® Standard De-Energized Visual Inspection Form | Medium-Voltage Induction Machine | MVIN | 70B-STANDARD | visualInspection
Physical condition | Physical condition
Indicating device status | Indicating device status
Labeling | Labeling
Grounding/bonding | Grounding/bonding
Machinery alignment | Machinery alignment | Intended where signs of misalignment exist.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Application | Application | Ensure the machinery is installed in accordance with the manufacturer’s listing and labeling and applicable codes/standards. | NFPA 70B® Standard De-Energized Visual Inspection Form | Medium-Voltage Synchronous Machine | MVSC | 70B-STANDARD | visualInspection
Physical condition | Physical condition
Indicating device status | Indicating device status
Labeling | Labeling
Grounding/bonding | Grounding/bonding
Machinery alignment | Machinery alignment | Intended where signs of misalignment exist.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Application | Application | Ensure the machinery is installed in accordance with the manufacturer’s listing and labeling and applicable codes/standards. | Basic Energized Visual Inspection Form | Low-Voltage Machine (<= 200hp) | LVMT-S | BASIC | visualInspection
Physical condition | Physical condition
Indicating device status | Indicating device status
Labeling | Labeling
Grounding/bonding | Grounding/bonding
Machinery alignment | Machinery alignment | Intended where signs of misalignment exist.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Application | Application | Ensure the machinery is installed in accordance with the manufacturer’s listing and labeling and applicable codes/standards. | Basic Energized Visual Inspection Form | Low-Voltage Machine (>200hp) | LVMT-L | BASIC | visualInspection
Physical condition | Physical condition
Indicating device status | Indicating device status
Labeling | Labeling
Grounding/bonding | Grounding/bonding
Machinery alignment | Machinery alignment | Intended where signs of misalignment exist.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Application | Application | Ensure the machinery is installed in accordance with the manufacturer’s listing and labeling and applicable codes/standards. | Basic Energized Visual Inspection Form | Low-Voltage Machine (dc) | LVMT-DC | BASIC | visualInspection
Physical condition | Physical condition
Indicating device status | Indicating device status
Labeling | Labeling
Grounding/bonding | Grounding/bonding
Machinery alignment | Machinery alignment | Intended where signs of misalignment exist.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Application | Application | Ensure the machinery is installed in accordance with the manufacturer’s listing and labeling and applicable codes/standards. | Basic Energized Visual Inspection Form | Medium-Voltage Induction Machine | MVIN | BASIC | visualInspection
Physical condition | Physical condition
Indicating device status | Indicating device status
Labeling | Labeling
Grounding/bonding | Grounding/bonding
Machinery alignment | Machinery alignment | Intended where signs of misalignment exist.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Application | Application | Ensure the machinery is installed in accordance with the manufacturer’s listing and labeling and applicable codes/standards. | Basic Energized Visual Inspection Form | Medium-Voltage Synchronous Machine | MVSC | BASIC | visualInspection
Physical condition | Physical condition
Indicating device status | Indicating device status
Labeling | Labeling
Grounding/bonding | Grounding/bonding
Machinery alignment | Machinery alignment | Intended where signs of misalignment exist.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, and insulating materials shall be kept clean to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Low-Voltage Machine (<= 200hp) | LVMT-S | 70B-ENHANCED | cleaning
Cleanliness | After cleaning, apparatus shall be dried before being placed in operation if tests indicate that the insulation resistance is below the recommended level.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, and insulating materials shall be kept clean to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Low-Voltage Machine (>200hp) | LVMT-L | 70B-ENHANCED | cleaning
Cleanliness | After cleaning, apparatus shall be dried before being placed in operation if tests indicate that the insulation resistance is below the recommended level.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, and insulating materials shall be kept clean to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Low-Voltage Machine (dc) | LVMT-DC | 70B-ENHANCED | cleaning
Cleanliness | After cleaning, apparatus shall be dried before being placed in operation if tests indicate that the insulation resistance is below the recommended level.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, and insulating materials shall be kept clean to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Medium-Voltage Induction Machine | MVIN | 70B-ENHANCED | cleaning
Cleanliness | After cleaning, apparatus shall be dried before being placed in operation if tests indicate that the insulation resistance is below the recommended level.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, and insulating materials shall be kept clean to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Medium-Voltage Synchronous Machine | MVSC | 70B-ENHANCED | cleaning
Cleanliness | After cleaning, apparatus shall be dried before being placed in operation if tests indicate that the insulation resistance is below the recommended level.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, and insulating materials shall be kept clean to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Standard De-Energized Cleaning Form | Low-Voltage Machine (<= 200hp) | LVMT-S | 70B-STANDARD | cleaning
Cleanliness | After cleaning, apparatus shall be dried before being placed in operation if tests indicate that the insulation resistance is below the recommended level.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, and insulating materials shall be kept clean to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Standard De-Energized Cleaning Form | Low-Voltage Machine (>200hp) | LVMT-L | 70B-STANDARD | cleaning
Cleanliness | After cleaning, apparatus shall be dried before being placed in operation if tests indicate that the insulation resistance is below the recommended level.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, and insulating materials shall be kept clean to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Standard De-Energized Cleaning Form | Low-Voltage Machine (dc) | LVMT-DC | 70B-STANDARD | cleaning
Cleanliness | After cleaning, apparatus shall be dried before being placed in operation if tests indicate that the insulation resistance is below the recommended level.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, and insulating materials shall be kept clean to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Standard De-Energized Cleaning Form | Medium-Voltage Induction Machine | MVIN | 70B-STANDARD | cleaning
Cleanliness | After cleaning, apparatus shall be dried before being placed in operation if tests indicate that the insulation resistance is below the recommended level.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, and insulating materials shall be kept clean to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a safety hazard. |  | NFPA 70B® Standard De-Energized Cleaning Form | Medium-Voltage Synchronous Machine | MVSC | 70B-STANDARD | cleaning
Cleanliness | After cleaning, apparatus shall be dried before being placed in operation if tests indicate that the insulation resistance is below the recommended level.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Bearings, couplings, and auxiliary devices shall be lubricated as needed. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Low-Voltage Machine (<= 200hp) | LVMT-S | 70B-ENHANCED | lubrication
Lubrication | Where equipped, lubrication systems shall be maintained in accordance with the manufacturer’s instructions.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Bearings, couplings, and auxiliary devices shall be lubricated as needed. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Low-Voltage Machine (>200hp) | LVMT-L | 70B-ENHANCED | lubrication
Lubrication | Where equipped, lubrication systems shall be maintained in accordance with the manufacturer’s instructions.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Bearings, couplings, and auxiliary devices shall be lubricated as needed. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Low-Voltage Machine (dc) | LVMT-DC | 70B-ENHANCED | lubrication
Lubrication | Where equipped, lubrication systems shall be maintained in accordance with the manufacturer’s instructions.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Bearings, couplings, and auxiliary devices shall be lubricated as needed. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Medium-Voltage Induction Machine | MVIN | 70B-ENHANCED | lubrication
Lubrication | Where equipped, lubrication systems shall be maintained in accordance with the manufacturer’s instructions.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Bearings, couplings, and auxiliary devices shall be lubricated as needed. |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Medium-Voltage Synchronous Machine | MVSC | 70B-ENHANCED | lubrication
Lubrication | Where equipped, lubrication systems shall be maintained in accordance with the manufacturer’s instructions.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Bearings, couplings, and auxiliary devices shall be lubricated as needed. |  | NFPA 70B® Standard De-Energized Lubrication Form | Low-Voltage Machine (<= 200hp) | LVMT-S | 70B-STANDARD | lubrication
Lubrication | Where equipped, lubrication systems shall be maintained in accordance with the manufacturer’s instructions.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Bearings, couplings, and auxiliary devices shall be lubricated as needed. |  | NFPA 70B® Standard De-Energized Lubrication Form | Low-Voltage Machine (>200hp) | LVMT-L | 70B-STANDARD | lubrication
Lubrication | Where equipped, lubrication systems shall be maintained in accordance with the manufacturer’s instructions.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Bearings, couplings, and auxiliary devices shall be lubricated as needed. |  | NFPA 70B® Standard De-Energized Lubrication Form | Low-Voltage Machine (dc) | LVMT-DC | 70B-STANDARD | lubrication
Lubrication | Where equipped, lubrication systems shall be maintained in accordance with the manufacturer’s instructions.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Bearings, couplings, and auxiliary devices shall be lubricated as needed. |  | NFPA 70B® Standard De-Energized Lubrication Form | Medium-Voltage Induction Machine | MVIN | 70B-STANDARD | lubrication
Lubrication | Where equipped, lubrication systems shall be maintained in accordance with the manufacturer’s instructions.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Bearings, couplings, and auxiliary devices shall be lubricated as needed. |  | NFPA 70B® Standard De-Energized Lubrication Form | Medium-Voltage Synchronous Machine | MVSC | 70B-STANDARD | lubrication
Lubrication | Where equipped, lubrication systems shall be maintained in accordance with the manufacturer’s instructions.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Integrity of accessible bolted connections |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Low-Voltage Machine (<= 200hp) | LVMT-S | 70B-ENHANCED | mechanicalServicing
Cooling system | Cooling system operation, as applicable
Operation | Mechanical operation
Guards | Machine guards and assemblies
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Integrity of accessible bolted connections |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Low-Voltage Machine (>200hp) | LVMT-L | 70B-ENHANCED | mechanicalServicing
Cooling system | Cooling system operation, as applicable
Operation | Mechanical operation
Guards | Machine guards and assemblies
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Integrity of accessible bolted connections |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Low-Voltage Machine (dc) | LVMT-DC | 70B-ENHANCED | mechanicalServicing
Cooling system | Cooling system operation, as applicable
Operation | Mechanical operation
Guards | Machine guards and assemblies
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Integrity of accessible bolted connections |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Medium-Voltage Induction Machine | MVIN | 70B-ENHANCED | mechanicalServicing
Cooling system | Cooling system operation, as applicable
Operation | Mechanical operation
Guards | Machine guards and assemblies
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Integrity of accessible bolted connections |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Medium-Voltage Synchronous Machine | MVSC | 70B-ENHANCED | mechanicalServicing
Cooling system | Cooling system operation, as applicable
Operation | Mechanical operation
Guards | Machine guards and assemblies
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Integrity of accessible bolted connections |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Low-Voltage Machine (<= 200hp) | LVMT-S | 70B-STANDARD | mechanicalServicing
Cooling system | Cooling system operation, as applicable
Operation | Mechanical operation
Guards | Machine guards and assemblies
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Integrity of accessible bolted connections |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Low-Voltage Machine (>200hp) | LVMT-L | 70B-STANDARD | mechanicalServicing
Cooling system | Cooling system operation, as applicable
Operation | Mechanical operation
Guards | Machine guards and assemblies
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Integrity of accessible bolted connections |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Low-Voltage Machine (dc) | LVMT-DC | 70B-STANDARD | mechanicalServicing
Cooling system | Cooling system operation, as applicable
Operation | Mechanical operation
Guards | Machine guards and assemblies
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Integrity of accessible bolted connections |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Medium-Voltage Induction Machine | MVIN | 70B-STANDARD | mechanicalServicing
Cooling system | Cooling system operation, as applicable
Operation | Mechanical operation
Guards | Machine guards and assemblies
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Integrity of accessible bolted connections |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Medium-Voltage Synchronous Machine | MVSC | 70B-STANDARD | mechanicalServicing
Cooling system | Cooling system operation, as applicable
Operation | Mechanical operation
Guards | Machine guards and assemblies
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Bolted connection resistance |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Low-Voltage Machine (<= 200hp) | LVMT-S | 70B-ENHANCED | electricalTesting
DAR | Stator/armature winding DAR | ac stator or dc armature
DAR | Wound rotor/field winding DAR | ac wound rotor, synchronous dc rotor, dc fields
PI | Stator/armature winding polarization index (PI)
PI | Wound rotor/field winding PI
Dielectric withstand | Stator winding dc dielectric withstand (overpotential)
Dielectric withstand | Wound rotor/field winding dc dielectric withstand (overpotential)
Winding resistance | Stator/armature winding resistance
Winding resistance | Wound rotor/field winding resistance
Surge | Stator winding surge comparison
Bearing insulation | Insulated bearing insulation resistance
Temperature detection | Temperature detection device
Space heater | Machine space heater
Vibration analysis | Vibration analysis* | *test conducted energized
Current analysis | Current signature analysis* | *test conducted energized
SPD | Surge protection device
Starter | Motor starter
CT | Current transformers
PT | Potential transformers
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Bolted connection resistance |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Low-Voltage Machine (>200hp) | LVMT-L | 70B-ENHANCED | electricalTesting
DAR | Stator/armature winding DAR | ac stator or dc armature
DAR | Wound rotor/field winding DAR | ac wound rotor, synchronous dc rotor, dc fields
PI | Stator/armature winding polarization index (PI)
PI | Wound rotor/field winding PI
Dielectric withstand | Stator winding dc dielectric withstand (overpotential)
Dielectric withstand | Wound rotor/field winding dc dielectric withstand (overpotential)
Winding resistance | Stator/armature winding resistance
Winding resistance | Wound rotor/field winding resistance
Surge | Stator winding surge comparison
Bearing insulation | Insulated bearing insulation resistance
Temperature detection | Temperature detection device
Space heater | Machine space heater
Vibration analysis | Vibration analysis* | *test conducted energized
Current analysis | Current signature analysis* | *test conducted energized
SPD | Surge protection device
Starter | Motor starter
CT | Current transformers
PT | Potential transformers
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Bolted connection resistance |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Low-Voltage Machine (dc) | LVMT-DC | 70B-ENHANCED | electricalTesting
DAR | Stator/armature winding DAR | ac stator or dc armature
DAR | Wound rotor/field winding DAR | ac wound rotor, synchronous dc rotor, dc fields
PI | Stator/armature winding polarization index (PI)
PI | Wound rotor/field winding PI
Dielectric withstand | Stator winding dc dielectric withstand (overpotential)
Dielectric withstand | Wound rotor/field winding dc dielectric withstand (overpotential)
Winding resistance | Stator/armature winding resistance
Winding resistance | Wound rotor/field winding resistance
Surge | Stator winding surge comparison
Bearing insulation | Insulated bearing insulation resistance
Temperature detection | Temperature detection device
Space heater | Machine space heater
Vibration analysis | Vibration analysis* | *test conducted energized
Current analysis | Current signature analysis* | *test conducted energized
Starter | Motor starter
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Bolted connection resistance |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Medium-Voltage Induction Machine | MVIN | 70B-ENHANCED | electricalTesting
DAR | Stator/armature winding DAR | ac stator or dc armature
DAR | Wound rotor/field winding DAR | ac wound rotor, synchronous dc rotor, dc fields
PI | Stator/armature winding polarization index (PI)
PI | Wound rotor/field winding PI
Dielectric withstand | Stator winding dc dielectric withstand (overpotential)
Dielectric withstand | Wound rotor/field winding dc dielectric withstand (overpotential)
Winding resistance | Stator/armature winding resistance
Winding resistance | Wound rotor/field winding resistance
Power factor | Stator winding insulation power factor | Insulation power factor/dissipation factor
Power factor | Stator winding insulation power factor tip-up | Insulation power factor/dissipation factor
Surge | Stator winding surge comparison
Bearing insulation | Insulated bearing insulation resistance
Temperature detection | Temperature detection device
Space heater | Machine space heater
Vibration analysis | Vibration analysis* | *test conducted energized
Current analysis | Current signature analysis* | *test conducted energized
Partial discharge | Partial discharge* | *test conducted energized
SPD | Surge protection device
Starter | Motor starter
CT | Current transformers
PT | Potential transformers
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Bolted connection resistance |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Medium-Voltage Synchronous Machine | MVSC | 70B-ENHANCED | electricalTesting
DAR | Stator/armature winding DAR | ac stator or dc armature
DAR | Wound rotor/field winding DAR | ac wound rotor, synchronous dc rotor, dc fields
PI | Stator/armature winding polarization index (PI)
Dielectric withstand | Stator winding dc dielectric withstand (overpotential)
Dielectric withstand | Wound rotor/field winding dc dielectric withstand (overpotential)
Winding resistance | Stator/armature winding resistance
Winding resistance | Wound rotor/field winding resistance
Power factor | Stator winding insulation power factor | Insulation power factor/dissipation factor
Power factor | Stator winding insulation power factor tip-up | Insulation power factor/dissipation factor
Surge | Stator winding surge comparison
Bearing insulation | Insulated bearing insulation resistance
Temperature detection | Temperature detection device
Space heater | Machine space heater
Vibration analysis | Vibration analysis* | *test conducted energized
Current analysis | Current signature analysis* | *test conducted energized
Partial discharge | Partial discharge* | *test conducted energized
SPD | Surge protection device
Starter | Motor starter
CT | Current transformers
PT | Potential transformers
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Space heater | Machine space heater |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Low-Voltage Machine (<= 200hp) | LVMT-S | 70B-STANDARD | electricalTesting
Starter | Motor starter
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Space heater | Machine space heater |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Low-Voltage Machine (>200hp) | LVMT-L | 70B-STANDARD | electricalTesting
Starter | Motor starter
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Space heater | Machine space heater |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Low-Voltage Machine (dc) | LVMT-DC | 70B-STANDARD | electricalTesting
Starter | Motor starter
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Bolted connection resistance |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Medium-Voltage Induction Machine | MVIN | 70B-STANDARD | electricalTesting
DAR | Stator/armature winding DAR | ac stator or dc armature
DAR | Wound rotor/field winding DAR | ac wound rotor, synchronous dc rotor, dc fields
PI | Stator/armature winding polarization index (PI)
Winding resistance | Stator/armature winding resistance
Winding resistance | Wound rotor/field winding resistance
Bearing insulation | Insulated bearing insulation resistance
Temperature detection | Temperature detection device
Space heater | Machine space heater
SPD | Surge protection device
Starter | Motor starter
CT | Current transformers
PT | Potential transformers
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Bolted connection resistance |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Medium-Voltage Synchronous Machine | MVSC | 70B-STANDARD | electricalTesting
DAR | Stator/armature winding DAR | ac stator or dc armature
DAR | Wound rotor/field winding DAR | ac wound rotor, synchronous dc rotor, dc fields
PI | Stator/armature winding polarization index (PI)
Winding resistance | Stator/armature winding resistance
Winding resistance | Wound rotor/field winding resistance
Bearing insulation | Insulated bearing insulation resistance
Temperature detection | Temperature detection device
Space heater | Machine space heater
SPD | Surge protection device
Starter | Motor starter
CT | Current transformers
PT | Potential transformers

## ch.29
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Condition | Inspect physical and mechanical condition |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Motor Control Equipment (<= 1000V) | MCEQ-LV | 70B-ENHANCED | visualInspection
Anchorage | Inspect anchorage and grounding
Contactors | Physical integrity of contactors
Sizing | Verify circuit breakers, fuses, and overload elements are the correct sizes and types and correspond to the drawings | EMP determines when these inspections can be done energized.
Instrument transformers | Verify instrument transformer ratios are correct
Insulators | Inspect insulators for damage, tracking, or contaminated surfaces
Filters | Verify filters are clean and in place
Phase barriers | Verify switch phase barriers are in place
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Condition | Inspect physical and mechanical condition |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Motor Control Equipment (> 1000V) | MCEQ-MV | 70B-ENHANCED | visualInspection
Anchorage | Inspect anchorage and grounding
Contactors | Physical integrity of contactors
Sizing | Verify circuit breakers, fuses, and overload elements are the correct sizes and types and correspond to the drawings | EMP determines when these inspections can be done energized.
Instrument transformers | Verify instrument transformer ratios are correct
Insulators | Inspect insulators for damage, tracking, or contaminated surfaces
Filters | Verify filters are clean and in place
Phase barriers | Verify switch phase barriers are in place
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Condition | Inspect physical and mechanical condition |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Motor Control Equipment (<= 1000V) | MCEQ-LV | 70B-STANDARD | visualInspection
Anchorage | Inspect anchorage and grounding
Contactors | Physical integrity of contactors
Sizing | Verify circuit breakers, fuses, and overload elements are the correct sizes and types and correspond to the drawings | EMP determines when these inspections can be done energized.
Instrument transformers | Verify instrument transformer ratios are correct
Insulators | Inspect insulators for damage, tracking, or contaminated surfaces
Filters | Verify filters are clean and in place
Phase barriers | Verify switch phase barriers are in place
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Condition | Inspect physical and mechanical condition |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Motor Control Equipment (> 1000V) | MCEQ-MV | 70B-STANDARD | visualInspection
Anchorage | Inspect anchorage and grounding
Contactors | Physical integrity of contactors
Sizing | Verify circuit breakers, fuses, and overload elements are the correct sizes and types and correspond to the drawings | EMP determines when these inspections can be done energized.
Instrument transformers | Verify instrument transformer ratios are correct
Insulators | Inspect insulators for damage, tracking, or contaminated surfaces
Filters | Verify filters are clean and in place
Phase barriers | Verify switch phase barriers are in place
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Condition | Inspect physical and mechanical condition |  | Basic Energized Visual Inspection Form | Motor Control Equipment (<= 1000V) | MCEQ-LV | BASIC | visualInspection
Anchorage | Inspect anchorage and grounding
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Condition | Inspect physical and mechanical condition |  | Basic Energized Visual Inspection Form | Motor Control Equipment (> 1000V) | MCEQ-MV | BASIC | visualInspection
Anchorage | Inspect anchorage and grounding
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Bus, cables, terminals or terminations, electrical equipment surfaces, enclosures, and insulating materials shall be cleaned to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a hazard. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Motor Control Equipment (<= 1000V) | MCEQ-LV | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Bus, cables, terminals or terminations, electrical equipment surfaces, enclosures, and insulating materials shall be cleaned to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a hazard. |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Motor Control Equipment (> 1000V) | MCEQ-MV | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Bus, cables, terminals or terminations, electrical equipment surfaces, enclosures, and insulating materials shall be cleaned to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a hazard. |  | NFPA 70B® Standard De-Energized Cleaning Form | Motor Control Equipment (<= 1000V) | MCEQ-LV | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Bus, cables, terminals or terminations, electrical equipment surfaces, enclosures, and insulating materials shall be cleaned to prevent a buildup of contaminants that negatively affect performance, reduce life expectancy, or create a hazard. |  | NFPA 70B® Standard De-Energized Cleaning Form | Motor Control Equipment (> 1000V) | MCEQ-MV | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed contacts as specified by the manufacturer |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Motor Control Equipment (<= 1000V) | MCEQ-LV | 70B-ENHANCED | lubrication
Lubrication | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces, as specified by the manufacturer
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed contacts as specified by the manufacturer |  | NFPA 70B® Enhanced De-Energized Lubrication Form | Motor Control Equipment (> 1000V) | MCEQ-MV | 70B-ENHANCED | lubrication
Lubrication | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces, as specified by the manufacturer
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed contacts as specified by the manufacturer |  | NFPA 70B® Standard De-Energized Lubrication Form | Motor Control Equipment (<= 1000V) | MCEQ-LV | 70B-STANDARD | lubrication
Lubrication | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces, as specified by the manufacturer
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Lubrication | Apply a thin coating of conductive lubricant to exposed contacts as specified by the manufacturer |  | NFPA 70B® Standard De-Energized Lubrication Form | Motor Control Equipment (> 1000V) | MCEQ-MV | 70B-STANDARD | lubrication
Lubrication | Apply nonconductive lubricant as needed to mechanism parts as specified by the manufacturer
Lubrication | Apply conductive lubricant to pivot points, as well as moving and sliding surfaces, as specified by the manufacturer
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Integrity of accessible bolted connections |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Motor Control Equipment (<= 1000V) | MCEQ-LV | 70B-ENHANCED | mechanicalServicing
Cooling system | Cooling system operation, as applicable
Operation | Mechanical operation
Guards | Machine guards and assemblies
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Integrity of accessible bolted connections |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Motor Control Equipment (> 1000V) | MCEQ-MV | 70B-ENHANCED | mechanicalServicing
Cooling system | Cooling system operation, as applicable
Operation | Mechanical operation
Guards | Machine guards and assemblies
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Integrity of accessible bolted connections |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Motor Control Equipment (<= 1000V) | MCEQ-LV | 70B-STANDARD | mechanicalServicing
Cooling system | Cooling system operation, as applicable
Operation | Mechanical operation
Guards | Machine guards and assemblies
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Bolted connections | Integrity of accessible bolted connections |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Motor Control Equipment (> 1000V) | MCEQ-MV | 70B-STANDARD | mechanicalServicing
Cooling system | Cooling system operation, as applicable
Operation | Mechanical operation
Guards | Machine guards and assemblies
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Inspect electrical connections for high resistance |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Motor Control Equipment (<= 1000V) | MCEQ-LV | 70B-ENHANCED | electricalTesting
Insulation resistance | Measure insulation resistance of electrical power circuits
Insulation resistance | Measure insulation resistance across each open starter pole
Insulation resistance | Measure insulation resistance of control wiring with respect to ground
Protective devices | Test motor protection devices
Operation | Perform control system operational tests | Include automatic throw-overs, paralleling controls, interlock and safety systems, or any other operational or maintenance-related control.
Dielectric withstand | Perform dielectric withstand test
Contact resistance | Measure contact resistance
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Inspect electrical connections for high resistance |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Motor Control Equipment (> 1000V) | MCEQ-MV | 70B-ENHANCED | electricalTesting
Insulation resistance | Measure insulation resistance of electrical power circuits
Insulation resistance | Measure insulation resistance across each open starter pole
Insulation resistance | Measure insulation resistance of control wiring with respect to ground
Protective devices | Test motor protection devices
Operation | Perform control system operational tests | Include automatic throw-overs, paralleling controls, interlock and safety systems, or any other operational or maintenance-related control.
Vacuum bottle | Perform vacuum bottle integrity test or a magnetron atmospheric condition (MAC) test on vacuum bottles
Dielectric withstand | Perform dielectric withstand test
Contact resistance | Measure contact resistance
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Inspect electrical connections for high resistance |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Motor Control Equipment (<= 1000V) | MCEQ-LV | 70B-STANDARD | electricalTesting
Insulation resistance | Measure insulation resistance of electrical power circuits
Insulation resistance | Measure insulation resistance across each open starter pole
Protective devices | Test motor protection devices
Contact resistance | Measure contact resistance
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Contact resistance | Inspect electrical connections for high resistance |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Motor Control Equipment (> 1000V) | MCEQ-MV | 70B-STANDARD | electricalTesting
Insulation resistance | Measure insulation resistance of electrical power circuits
Insulation resistance | Measure insulation resistance across each open starter pole
Protective devices | Test motor protection devices
Vacuum bottle | Perform vacuum bottle integrity test or a magnetron atmospheric condition (MAC) test on vacuum bottles
Contact resistance | Measure contact resistance

## ch.30
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
PV | Front of PV modules | Damage, debris, soiling, discoloration, cracks, and broken glass. | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Solar Photovoltaic System | SOLR | 70B-ENHANCED | visualInspection
PV | Backs of PV modules | Damage, debris, discoloration, cracks, and tears.
Shading | No unintentional shading of the array | Foliage, weeds, trees, or structures.
Conductors | Conductors, connectors, and wiring harnesses are secured | Damaged insulation, melted plastic, broken or missing wiring and raceway supports.
Signage | Signage, markings, and labels | Arc flash, shock, mechanical hazards, means of isolation location.
Sizing | String fuses are sized in accordance with system design | Array fires can be caused by improperly sized string fuses. Replacement fuses should be matched to the design criteria.
Enclosures | Ensure all electrical equipment enclosures, raceways, structures, and mechanical apparatus are secured | Loose connections or connectors, broken raceways, and supports, missing hardware.
Systems | Tracking and mechanical systems (e.g., gearbox, drivetrain) | Leaking fluids, bent, broken or damaged drivetrains, array alignment.
Grounding | Grounding and bonding | Secure attachment, missing, damaged or broken connections, protection from physical damage.
Cells | Battery cells and jumpers | Leaking, bulging, corrosion, fluid levels, damage, melted plastic, discoloration.
Roof | Roof or wall penetrations | Moisture, dust, and dirt ingress.
Site | Site | Storm water runoff channels clear of debris, erosion around piers and pads, vegetation management, animal infestation/nesting/burrowing.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
PV | Front of PV modules | Damage, debris, soiling, discoloration, cracks, and broken glass. | NFPA 70B® Standard De-Energized Visual Inspection Form | Solar Photovoltaic System | SOLR | 70B-STANDARD | visualInspection
PV | Backs of PV modules | Damage, debris, discoloration, cracks, and tears.
Shading | No unintentional shading of the array | Foliage, weeds, trees, or structures.
Conductors | Conductors, connectors, and wiring harnesses are secured | Damaged insulation, melted plastic, broken or missing wiring and raceway supports.
Signage | Signage, markings, and labels | Arc flash, shock, mechanical hazards, means of isolation location.
Enclosures | Ensure all electrical equipment enclosures, raceways, structures, and mechanical apparatus are secured | Loose connections or connectors, broken raceways, and supports, missing hardware.
Systems | Tracking and mechanical systems (e.g., gearbox, drivetrain) | Leaking fluids, bent, broken or damaged drivetrains, array alignment.
Grounding | Grounding and bonding | Secure attachment, missing, damaged or broken connections, protection from physical damage.
Cells | Battery cells and jumpers | Leaking, bulging, corrosion, fluid levels, damage, melted plastic, discoloration.
Roof | Roof or wall penetrations | Moisture, dust, and dirt ingress.
Site | Site | Storm water runoff channels clear of debris, erosion around piers and pads, vegetation management, animal infestation/nesting/burrowing.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Sizing | String fuses are sized in accordance with system design | Array fires can be caused by improperly sized string fuses. Replacement fuses should be matched to the design criteria. | Basic Energized Visual Inspection Form | Solar Photovoltaic System | SOLR | BASIC | visualInspection
Terminations | Electrical terminations, module interconnections | Damage, corrosion, discoloration.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Mechanical | Tracking and mechanical systems (e.g., gearbox, drivetrain) | Torque of bolted mechanical systems, mechanical alignment. | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Solar Photovoltaic System | SOLR | 70B-ENHANCED | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Mechanical | Tracking and mechanical systems (e.g., gearbox, drivetrain) | Torque of bolted mechanical systems, mechanical alignment. | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Solar Photovoltaic System | SOLR | 70B-STANDARD | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Mechanical | Tracking and mechanical systems (e.g., gearbox, drivetrain) | Torque of bolted mechanical systems, mechanical alignment. | Basic Energized Mechanical Servicing Form | Solar Photovoltaic System | SOLR | BASIC | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Terminations | Electrical terminations | Any or all the following could be utilized: infrared thermography, contact resistance, millivolt drop, calibrated torque device. | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Solar Photovoltaic System | SOLR | 70B-ENHANCED | electricalTesting
Grounding | Grounding and bonding | Any or all the following could be utilized: infrared thermography, contact resistance, fall of potential, point to point, current reading, calibrated torque device.
PV Strings | PV strings and modules | IV curve trace, insulation resistance, operating voltage, and current readings, electroluminescence imaging, infrared thermography.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Terminations | Electrical terminations | Any or all the following could be utilized: infrared thermography, contact resistance, millivolt drop, calibrated torque device. | NFPA 70B® Standard De-Energized Electrical Testing Form | Solar Photovoltaic System | SOLR | 70B-STANDARD | electricalTesting
Grounding | Grounding and bonding | Any or all the following could be utilized: infrared thermography, contact resistance, fall of potential, point to point, current reading, calibrated torque device.
PV Strings | PV strings and modules | IV curve trace, insulation resistance, operating voltage, and current readings, electroluminescence imaging, infrared thermography.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Terminations | Electrical terminations | Any or all the following could be utilized: infrared thermography, contact resistance, millivolt drop, calibrated torque device. | Basic Energized Electrical Testing Form | Solar Photovoltaic System | SOLR | BASIC | electricalTesting
Grounding | Grounding and bonding | Any or all the following could be utilized: infrared thermography, contact resistance, fall of potential, point to point, current reading, calibrated torque device.
PV Strings | PV strings and modules | IV curve trace, insulation resistance, operating voltage, and current readings, electroluminescence imaging, infrared thermography.

## ch.31
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Grounding | Grounding and bonding |  | NFPA 70B® Enhanced Visual / Mechanical Inspection Form | Wind Power System | WIND | 70B-ENHANCED | visualInspection
Lights | Functional navigational warning lights
Weather measurement | Weather measurement devices
Lightning protection | Lightning protection
Yaw systems | Check yaw systems for damage, wear, and signs of overheating
Pitch systems | Check pitch systems for damage, wear, and signs of overheating
Cables | Check cables, terminations, and cable support systems for:
Cables | Check cables, terminations, and calbe support systems for: Structural integrity
Cables | Check cables, terminations, and calbe support systems for: Signs of vibration damage or abrasion
Cables | Check cables, terminations, and calbe support systems for: Overheating
Lights | In-tower emergency lighting is functioning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Grounding | Grounding and bonding |  | NFPA 70B® Standard Visual / Mechanical Inspection Form | Wind Power System | WIND | 70B-STANDARD | visualInspection
Lights | Functional navigational warning lights
Weather measurement | Weather measurement devices
Lightning protection | Lightning protection
Yaw systems | Check yaw systems for damage, wear, and signs of overheating
Pitch systems | Check pitch systems for damage, wear, and signs of overheating
Cables | Check cables, terminations, and cable support systems for:
Cables | Check cables, terminations, and calbe support systems for: Structural integrity
Cables | Check cables, terminations, and calbe support systems for: Signs of vibration damage or abrasion
Cables | Check cables, terminations, and calbe support systems for: Overheating
Lights | In-tower emergency lighting is functioning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Grounding | Grounding and bonding |  | Basic Visual / Mechanical Inspection Form | Wind Power System | WIND | BASIC | visualInspection
Lights | Functional navigational warning lights
Weather measurement | Weather measurement devices
Lightning protection | Lightning protection
Yaw systems | Check yaw systems for damage, wear, and signs of overheating
Pitch systems | Check pitch systems for damage, wear, and signs of overheating
Cables | Check cables, terminations, and cable support systems for:
Cables | Check cables, terminations, and calbe support systems for: Structural integrity
Cables | Check cables, terminations, and calbe support systems for: Signs of vibration damage or abrasion
Cables | Check cables, terminations, and calbe support systems for: Overheating
Lights | In-tower emergency lighting is functioning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Groudning electrode | Check grounding electrode system resistance |  | NFPA 70B® Enhanced Electrical Testing Form | Wind Power System | WIND | 70B-ENHANCED | electricalTesting
Emergency stops | Check emergency stops, safety shutdowns, controls, and warning indicators are functional
Supervisory control | Verify supervisory control and data acquisition (SCADA) systems are functional
Blade heat trace systems | Check functionality of blade heat trace systems, if installed
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Groudning electrode | Check grounding electrode system resistance |  | NFPA 70B® Standard Electrical Testing Form | Wind Power System | WIND | 70B-STANDARD | electricalTesting
Emergency stops | Check emergency stops, safety shutdowns, controls, and warning indicators are functional
Supervisory control | Verify supervisory control and data acquisition (SCADA) systems are functional
Blade heat trace systems | Check functionality of blade heat trace systems, if installed
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Groudning electrode | Check grounding electrode system resistance |  | Basic Electrical Testing Form | Wind Power System | WIND | BASIC | electricalTesting
Emergency stops | Check emergency stops, safety shutdowns, controls, and warning indicators are functional
Supervisory control | Verify supervisory control and data acquisition (SCADA) systems are functional
Blade heat trace systems | Check functionality of blade heat trace systems, if installed

## ch.32
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Condition | Physical condition, including operating environment | Damage or deterioration, supports or restraints, bending radius, excessive tension, signs of overheating. | NFPA 70B® Enhanced Visual Inspection Form | Battery Energy Storage System (ESS) | BESS | 70B-ENHANCED | visualInspection
Labeling | Correct labeling or identification | Phasing, cable ID, multiple sources, hazard, or other warning labels.
Grounding | Grounding/bonding | Damage, missing or loose terminations, clearance from energized parts, protection from physical damage.
Batteries | Batteries | Damage, leaking, swelling, discolored or melted plastic, terminal corrosion, electrolyte level, restraint systems.
Cables | Cables | Damage, deterioration, supports, bending radius, excessive tension, discoloration, or evidence of overheating.
Alarms | Fire alarm notification, detection, and suppression systems | Damaged heads, physical obstruction to spray, leaking, corrosion, suppression agent is charged.
Raceway | Raceway/cable tray | Damage or deterioration, cable jacket abrasion or wear when exposed, continuity, tight joints, missing or loose bonding jumpers, corrosion.
Barriers | Barriers, guards, and assemblies | Damage or signs of deterioration, arcing, tracking, supports, and mounting hardware.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Condition | Physical condition, including operating environment | Damage or deterioration, supports or restraints, bending radius, excessive tension, signs of overheating. | NFPA 70B® Standard Visual Inspection Form | Battery Energy Storage System (ESS) | BESS | 70B-STANDARD | visualInspection
Labeling | Correct labeling or identification | Phasing, cable ID, multiple sources, hazard, or other warning labels.
Grounding | Grounding/bonding | Damage, missing or loose terminations, clearance from energized parts, protection from physical damage.
Batteries | Batteries | Damage, leaking, swelling, discolored or melted plastic, terminal corrosion, electrolyte level, restraint systems.
Cables | Cables | Damage, deterioration, supports, bending radius, excessive tension, discoloration, or evidence of overheating.
Alarms | Fire alarm notification, detection, and suppression systems | Damaged heads, physical obstruction to spray, leaking, corrosion, suppression agent is charged.
Raceway | Raceway/cable tray | Damage or deterioration, cable jacket abrasion or wear when exposed, continuity, tight joints, missing or loose bonding jumpers, corrosion.
Barriers | Barriers, guards, and assemblies | Damage or signs of deterioration, arcing, tracking, supports, and mounting hardware.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Condition | Physical condition, including operating environment | Damage or deterioration, supports or restraints, bending radius, excessive tension, signs of overheating. | Basic Visual Inspection Form | Battery Energy Storage System (ESS) | BESS | BASIC | visualInspection
Labeling | Correct labeling or identification | Phasing, cable ID, multiple sources, hazard, or other warning labels.
Grounding | Grounding/bonding | Damage, missing or loose terminations, clearance from energized parts, protection from physical damage.
Batteries | Batteries | Damage, leaking, swelling, discolored or melted plastic, terminal corrosion, electrolyte level, restraint systems.
Cables | Cables | Damage, deterioration, supports, bending radius, excessive tension, discoloration, or evidence of overheating.
Alarms | Fire alarm notification, detection, and suppression systems | Damaged heads, physical obstruction to spray, leaking, corrosion, suppression agent is charged.
Raceway | Raceway/cable tray | Damage or deterioration, cable jacket abrasion or wear when exposed, continuity, tight joints, missing or loose bonding jumpers, corrosion.
Barriers | Barriers, guards, and assemblies | Damage or signs of deterioration, arcing, tracking, supports, and mounting hardware.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, insulating materials, terminals, or terminations shall be kept in a clean and contaminant-free state. |  | NFPA 70B® Enhanced Cleaning Form | Battery Energy Storage System (ESS) | BESS | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, insulating materials, terminals, or terminations shall be kept in a clean and contaminant-free state. |  | NFPA 70B® Standard Cleaning Form | Battery Energy Storage System (ESS) | BESS | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Electrical equipment surfaces, enclosures, insulating materials, terminals, or terminations shall be kept in a clean and contaminant-free state. |  | Basic Cleaning Form | Battery Energy Storage System (ESS) | BESS | BASIC | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | The ventilation system shall be serviced to ensure that airflow is maintained in accordance with the design requirements. |  | NFPA 70B® Enhanced Mechanical Servicing Form | Battery Energy Storage System (ESS) | BESS | 70B-ENHANCED | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | The ventilation system shall be serviced to ensure that airflow is maintained in accordance with the design requirements. |  | NFPA 70B® Standard Mechanical Servicing Form | Battery Energy Storage System (ESS) | BESS | 70B-STANDARD | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | The ventilation system shall be serviced to ensure that airflow is maintained in accordance with the design requirements. |  | Basic Mechanical Servicing Form | Battery Energy Storage System (ESS) | BESS | BASIC | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Ultrasonic | Airborne ultrasonic acoustic emissions |  | NFPA 70B® Enhanced Electrical Testing Form | Battery Energy Storage System (ESS) | BESS | 70B-ENHANCED | electricalTesting
Insulation resistance | Insulation resistance
Contact resistance | Bolted connection resistance
Battery performance | Battery performance test
System data | Review of battery management system data and associated alarms
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Insulation resistance | Insulation resistance |  | NFPA 70B® Standard Electrical Testing Form | Battery Energy Storage System (ESS) | BESS | 70B-STANDARD | electricalTesting
Contact resistance | Bolted connection resistance
Battery performance | Battery performance test
System data | Review of battery management system data and associated alarms
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Insulation resistance | Bolted connection resistance |  | Basic Electrical Testing Form | Battery Energy Storage System (ESS) | BESS | BASIC | electricalTesting
System data | Review of battery management system data and associated alarms

## ch.33
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors | Inspect doors and latches for fit, dents, corrosion, and missing hardware | Damage or deterioration, supports or restraints. | NFPA 70B® Enhanced Visual Inspection Form | Electrical Vehicle Charging Station | EVCS | 70B-ENHANCED | visualInspection
Wiring | Inspect wiring, bus, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition including corrosion | Excessive tension, signs of overheating, multiple sources, hazard, or other warning labels.
Grounding | Inspect grounding/bonding | Damage, missing or loose terminations, clearance from energized parts, protection from physical damage.
Cables | Inspect cables | Damage, deterioration, supports, bending radius, excessive tension, cable ID, discoloration, cable jacket abrasion or wear when exposed, or evidence of overheating.
Raceway | Inspect raceway/cable tray | Damage or deterioration, cable jacket abrasion or wear when exposed, continuity, tight joints, missing or loose bonding jumpers, corrosion.
Barriers | Inspect barriers, guards, and assemblies | Damage or signs of deterioration, arcing, tracking, supports and mounting hardware.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors | Inspect doors and latches for fit, dents, corrosion, and missing hardware | Damage or deterioration, supports or restraints. | NFPA 70B® Standard Visual Inspection Form | Electrical Vehicle Charging Station | EVCS | 70B-STANDARD | visualInspection
Wiring | Inspect wiring, bus, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition including corrosion | Excessive tension, signs of overheating, multiple sources, hazard, or other warning labels.
Grounding | Inspect grounding/bonding | Damage, missing or loose terminations, clearance from energized parts, protection from physical damage.
Cables | Inspect cables | Damage, deterioration, supports, bending radius, excessive tension, cable ID, discoloration, cable jacket abrasion or wear when exposed, or evidence of overheating.
Raceway | Inspect raceway/cable tray | Damage or deterioration, cable jacket abrasion or wear when exposed, continuity, tight joints, missing or loose bonding jumpers, corrosion.
Barriers | Inspect barriers, guards, and assemblies | Damage or signs of deterioration, arcing, tracking, supports and mounting hardware.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Doors | Inspect doors and latches for fit, dents, corrosion, and missing hardware | Damage or deterioration, supports or restraints. | Basic Visual Inspection Form | Electrical Vehicle Charging Station | EVCS | BASIC | visualInspection
Wiring | Inspect wiring, bus, and connections for damaged insulation, broken leads, tightness of connections, crimping, and overall general condition including corrosion | Excessive tension, signs of overheating, multiple sources, hazard, or other warning labels.
Grounding | Inspect grounding/bonding | Damage, missing or loose terminations, clearance from energized parts, protection from physical damage.
Cables | Inspect cables | Damage, deterioration, supports, bending radius, excessive tension, cable ID, discoloration, cable jacket abrasion or wear when exposed, or evidence of overheating.
Raceway | Inspect raceway/cable tray | Damage or deterioration, cable jacket abrasion or wear when exposed, continuity, tight joints, missing or loose bonding jumpers, corrosion.
Barriers | Inspect barriers, guards, and assemblies | Damage or signs of deterioration, arcing, tracking, supports and mounting hardware.

## ch.35
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Case and windows | Inspect case and windows for cracks and proper seal |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Electromechanical Relay | EMRE | 70B-ENHANCED | visualInspection
CT shorting blocks | Inspect current transformer shorting blocks and voltage disconnects
LEDs | Check for proper operation of LEDs, targets, and visual displays
Wiring | Inspect wiring and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition including corrosion
Clearances | Inspect clearances, mechanical freedom, and condition of contacts and control springs
Contact bearing clearances | Inspect contact bearing clearances and freedom of movement
Settings | Check that settings are in accordance with coordination study
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Case and windows | Inspect case and windows for cracks and proper seal |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Solid-State Relay | SSRE | 70B-ENHANCED | visualInspection
CT shorting blocks | Inspect current transformer shorting blocks and voltage disconnects
LEDs | Check for proper operation of LEDs, targets, and visual displays
Wiring | Inspect wiring and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition including corrosion
Settings | Check that settings are in accordance with coordination study
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Case and windows | Inspect case and windows for cracks and proper seal |  | NFPA 70B® Enhanced De-Energized Visual Inspection Form | Microprocessor Relay | MPRE | 70B-ENHANCED | visualInspection
CT shorting blocks | Inspect current transformer shorting blocks and voltage disconnects
LEDs | Check for proper operation of LEDs, targets, and visual displays
Wiring | Inspect wiring and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition including corrosion
Settings | Check that settings are in accordance with coordination study
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Case and windows | Inspect case and windows for cracks and proper seal |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Electromechanical Relay | EMRE | 70B-STANDARD | visualInspection
CT shorting blocks | Inspect current transformer shorting blocks and voltage disconnects
LEDs | Check for proper operation of LEDs, targets, and visual displays
Wiring | Inspect wiring and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition including corrosion
Clearances | Inspect clearances, mechanical freedom, and condition of contacts and control springs
Contact bearing clearances | Inspect contact bearing clearances and freedom of movement
Settings | Check that settings are in accordance with coordination study
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Case and windows | Inspect case and windows for cracks and proper seal |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Solid-State Relay | SSRE | 70B-STANDARD | visualInspection
CT shorting blocks | Inspect current transformer shorting blocks and voltage disconnects
LEDs | Check for proper operation of LEDs, targets, and visual displays
Wiring | Inspect wiring and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition including corrosion
Settings | Check that settings are in accordance with coordination study
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Case and windows | Inspect case and windows for cracks and proper seal |  | NFPA 70B® Standard De-Energized Visual Inspection Form | Microprocessor Relay | MPRE | 70B-STANDARD | visualInspection
CT shorting blocks | Inspect current transformer shorting blocks and voltage disconnects
LEDs | Check for proper operation of LEDs, targets, and visual displays
Wiring | Inspect wiring and connections for damaged insulation, broken leads, tightness of connections, proper crimping, and overall general condition including corrosion
Settings | Check that settings are in accordance with coordination study
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the relay case and cover |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Electromechanical Relay | EMRE | 70B-ENHANCED | cleaning
Cleanliness | Clean relay contacts, disks, and magnets
Cleanliness | Burnish burned or pitted contacts
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the relay case and cover |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Solid-State Relay | SSRE | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the relay case and cover |  | NFPA 70B® Enhanced De-Energized Cleaning Form | Microprocessor Relay | MPRE | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the relay case and cover |  | NFPA 70B® Standard De-Energized Cleaning Form | Electromechanical Relay | EMRE | 70B-STANDARD | cleaning
Cleanliness | Clean relay contacts, disks, and magnets
Cleanliness | Burnish burned or pitted contacts
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the relay case and cover |  | NFPA 70B® Standard De-Energized Cleaning Form | Solid-State Relay | SSRE | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Clean the relay case and cover |  | NFPA 70B® Standard De-Energized Cleaning Form | Microprocessor Relay | MPRE | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Relay disks | Check relay disks for friction, freedom of movement, correct travel, and clearance. |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Electromechanical Relay | EMRE | 70B-ENHANCED | mechanicalServicing
Target and reset | Operate targets and reset mechanisms.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Target and reset | Operate targets and reset mechanisms. |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Solid-State Relay | SSRE | 70B-ENHANCED | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
System update | Update to most current firmware. |  | NFPA 70B® Enhanced De-Energized Mechanical Servicing Form | Microprocessor Relay | MPRE | 70B-ENHANCED | mechanicalServicing
Trip and close coil | Check trip and close coil monitoring functions.
CB monitoring | Check circuit breaker monitoring.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Relay disks | Check relay disks for friction, freedom of movement, correct travel, and clearance. |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Electromechanical Relay | EMRE | 70B-STANDARD | mechanicalServicing
Target and reset | Operate targets and reset mechanisms.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Target and reset | Operate targets and reset mechanisms. |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Solid-State Relay | SSRE | 70B-STANDARD | mechanicalServicing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Trip and close coil | Check trip and close coil monitoring functions. |  | NFPA 70B® Standard De-Energized Mechanical Servicing Form | Microprocessor Relay | MPRE | 70B-STANDARD | mechanicalServicing
CB monitoring | Check circuit breaker monitoring.
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Insulation resistnace | Perform an insulation resistance test on each branch circuit to frame |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Electromechanical Relay | EMRE | 70B-ENHANCED | electricalTesting
Pickup | Perform a pickup test to determine the minimum or maximum current, voltage, power, or frequency that causes closure of relay contacts for all active functions
Timing | Perform a timing at three points on the time dial curve to verify the timing characteristics of the relay
Operation | Perform tests as required to check operation of restraint, directional, and other protective elements
Zero check | Perform a zero check test to determine proper time dial position when the relay is fixed and moving contacts are closed by the manual rotation of the time dial towards zero
Input output | Verify each input and output performs the intended function in accordance with control drawings
Clear trip counters | After testing is complete, clear trip counters, targets, events, and oscillographs from testing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Pickup | Perform a pickup test to determine the minimum or maximum current, voltage, power, or frequency that causes closure of relay contacts for all active functions |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Solid-State Relay | SSRE | 70B-ENHANCED | electricalTesting
Timing | Perform a timing at three points on the time dial curve to verify the timing characteristics of the relay
Operation | Perform tests as required to check operation of restraint, directional, and other protective elements
Input output | Verify each input and output performs the intended function in accordance with control drawings
Clear trip counters | After testing is complete, clear trip counters, targets, events, and oscillographs from testing
Review maintenance data | Review maintenance and statistical data
Settings and parameter changes | Download or document settings, logic, and other parameters when changes are made
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Pickup | Perform a pickup test to determine the minimum or maximum current, voltage, power, or frequency that causes closure of relay contacts for all active functions |  | NFPA 70B® Enhanced De-Energized Electrical Testing Form | Microprocessor Relay | MPRE | 70B-ENHANCED | electricalTesting
Timing | Perform a timing at three points on the time dial curve to verify the timing characteristics of the relay
Operation | Perform tests as required to check operation of restraint, directional, and other protective elements
Relay checks | Perform relay checks to verify relay status, meter readings (if applicable), and contact inputs/outputs
Arc reduction technology | Test arc energy reduction technology in accordance with the manufacturer’s instructions
Input output | Verify each input and output performs the intended function in accordance with control drawings
Clear trip counters | After testing is complete, clear trip counters, targets, events, and oscillographs from testing
Review maintenance data | Review maintenance and statistical data
Settings and parameter changes | Download or document settings, logic, and other parameters when changes are made
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Insulation resistnace | Perform an insulation resistance test on each branch circuit to frame |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Electromechanical Relay | EMRE | 70B-STANDARD | electricalTesting
Pickup | Perform a pickup test to determine the minimum or maximum current, voltage, power, or frequency that causes closure of relay contacts for all active functions
Timing | Perform a timing at three points on the time dial curve to verify the timing characteristics of the relay
Operation | Perform tests as required to check operation of restraint, directional, and other protective elements
Zero check | Perform a zero check test to determine proper time dial position when the relay is fixed and moving contacts are closed by the manual rotation of the time dial towards zero
Clear trip counters | After testing is complete, clear trip counters, targets, events, and oscillographs from testing
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Pickup | Perform a pickup test to determine the minimum or maximum current, voltage, power, or frequency that causes closure of relay contacts for all active functions |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Solid-State Relay | SSRE | 70B-STANDARD | electricalTesting
Timing | Perform a timing at three points on the time dial curve to verify the timing characteristics of the relay
Operation | Perform tests as required to check operation of restraint, directional, and other protective elements
Clear trip counters | After testing is complete, clear trip counters, targets, events, and oscillographs from testing
Review maintenance data | Review maintenance and statistical data
Settings and parameter changes | Download or document settings, logic, and other parameters when changes are made
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Relay checks | Perform relay checks to verify relay status, meter readings (if applicable), and contact inputs/outputs |  | NFPA 70B® Standard De-Energized Electrical Testing Form | Microprocessor Relay | MPRE | 70B-STANDARD | electricalTesting
Arc reduction technology | Test arc energy reduction technology in accordance with the manufacturer’s instructions
Review maintenance data | Review maintenance and statistical data
Settings and parameter changes | Download or document settings, logic, and other parameters when changes are made

## ch.36
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Battery performance | Conduct battery performance tests |  | NFPA 70B® Enhanced Battery Performance Testing Form | Vented Lead-Acid Battery | VLAB | 70B-ENHANCED | batteryPerformanceTesting
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Battery performance | Conduct battery performance tests |  | NFPA 70B® Enhanced Battery Performance Testing Form | Valve-Regulated Lead-Acid Battery | VRLB | 70B-ENHANCED | batteryPerformanceTesting
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Battery performance | Conduct battery performance tests |  | NFPA 70B® Enhanced Battery Performance Testing Form | Ni-Cad Battery | NICB | 70B-ENHANCED | batteryPerformanceTesting
issueTItle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Containers | Inspect containers, covers, and vent caps for cracks and structural damage |  | NFPA 70B® Enhanced Visual Inspection Form | Vented Lead-Acid Battery | VLAB | 70B-ENHANCED | visualInspection
Plates | Inspect plates and internal parts when visible | Document excessive positive plate growth, sulfate crystal formation, buckling, warping, scaling, swelling, cracking, hydration rings, excessive sedimentation, mossing, copper contamination, internal post seal cracks, and changes in color.
Cables | Inspect interconnection cables, cell connectors, and other conductors for wear, contamination, corrosion, and discoloration
Racks | Inspect battery racks for corrosion, cleanliness, proper grounding, and structural integrity, seismic protection
Electrolyte | Inspect electrolyte for containment, leaking, spills, and levels
Ventilation | Inspect ventilation equipment operation, dampers, filters, alarms, and other items that might restrict air movement
Heating | Inspect heating and air conditioning equipment including filters that control ambient room temperature for restricted air movement
Lights | Verify the functionality of lights, strobes, horns, and related alarm notifications
issueTItle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Containers | Inspect containers, covers, and vent caps for cracks and structural damage |  | NFPA 70B® Enhanced Visual Inspection Form | Valve-Regulated Lead-Acid Battery | VRLB | 70B-ENHANCED | visualInspection
Plates | Inspect plates and internal parts when visible | Document excessive positive plate growth, sulfate crystal formation, buckling, warping, scaling, swelling, cracking, hydration rings, excessive sedimentation, mossing, copper contamination, internal post seal cracks, and changes in color.
Cables | Inspect interconnection cables, cell connectors, and other conductors for wear, contamination, corrosion, and discoloration
Racks | Inspect battery racks for corrosion, cleanliness, proper grounding, and structural integrity, seismic protection
Electrolyte | Inspect electrolyte for containment, leaking, spills, and levels
Ventilation | Inspect ventilation equipment operation, dampers, filters, alarms, and other items that might restrict air movement
Heating | Inspect heating and air conditioning equipment including filters that control ambient room temperature for restricted air movement
Lights | Verify the functionality of lights, strobes, horns, and related alarm notifications
issueTItle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Containers | Inspect containers, covers, and vent caps for cracks and structural damage |  | NFPA 70B® Enhanced Visual Inspection Form | Ni-Cad Battery | NICB | 70B-ENHANCED | visualInspection
Plates | Inspect plates and internal parts when visible | Document excessive positive plate growth, sulfate crystal formation, buckling, warping, scaling, swelling, cracking, hydration rings, excessive sedimentation, mossing, copper contamination, internal post seal cracks, and changes in color.
Cables | Inspect interconnection cables, cell connectors, and other conductors for wear, contamination, corrosion, and discoloration
Racks | Inspect battery racks for corrosion, cleanliness, proper grounding, and structural integrity, seismic protection
Electrolyte | Inspect electrolyte for containment, leaking, spills, and levels
Ventilation | Inspect ventilation equipment operation, dampers, filters, alarms, and other items that might restrict air movement
Heating | Inspect heating and air conditioning equipment including filters that control ambient room temperature for restricted air movement
Lights | Verify the functionality of lights, strobes, horns, and related alarm notifications
issueTItle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Containers | Inspect containers, covers, and vent caps for cracks and structural damage |  | NFPA 70B® Standard Visual Inspection Form | Vented Lead-Acid Battery | VLAB | 70B-STANDARD | visualInspection
Plates | Inspect plates and internal parts when visible | Document excessive positive plate growth, sulfate crystal formation, buckling, warping, scaling, swelling, cracking, hydration rings, excessive sedimentation, mossing, copper contamination, internal post seal cracks, and changes in color.
Cables | Inspect interconnection cables, cell connectors, and other conductors for wear, contamination, corrosion, and discoloration
Racks | Inspect battery racks for corrosion, cleanliness, proper grounding, and structural integrity, seismic protection
Electrolyte | Inspect electrolyte for containment, leaking, spills, and levels
Ventilation | Inspect ventilation equipment operation, dampers, filters, alarms, and other items that might restrict air movement
Heating | Inspect heating and air conditioning equipment including filters that control ambient room temperature for restricted air movement
Lights | Verify the functionality of lights, strobes, horns, and related alarm notifications
issueTItle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Containers | Inspect containers, covers, and vent caps for cracks and structural damage |  | NFPA 70B® Standard Visual Inspection Form | Valve-Regulated Lead-Acid Battery | VRLB | 70B-STANDARD | visualInspection
Plates | Inspect plates and internal parts when visible | Document excessive positive plate growth, sulfate crystal formation, buckling, warping, scaling, swelling, cracking, hydration rings, excessive sedimentation, mossing, copper contamination, internal post seal cracks, and changes in color.
Cables | Inspect interconnection cables, cell connectors, and other conductors for wear, contamination, corrosion, and discoloration
Racks | Inspect battery racks for corrosion, cleanliness, proper grounding, and structural integrity, seismic protection
Electrolyte | Inspect electrolyte for containment, leaking, spills, and levels
Ventilation | Inspect ventilation equipment operation, dampers, filters, alarms, and other items that might restrict air movement
Heating | Inspect heating and air conditioning equipment including filters that control ambient room temperature for restricted air movement
Lights | Verify the functionality of lights, strobes, horns, and related alarm notifications
issueTItle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Containers | Inspect containers, covers, and vent caps for cracks and structural damage |  | NFPA 70B® Standard Visual Inspection Form | Ni-Cad Battery | NICB | 70B-STANDARD | visualInspection
Plates | Inspect plates and internal parts when visible | Document excessive positive plate growth, sulfate crystal formation, buckling, warping, scaling, swelling, cracking, hydration rings, excessive sedimentation, mossing, copper contamination, internal post seal cracks, and changes in color.
Cables | Inspect interconnection cables, cell connectors, and other conductors for wear, contamination, corrosion, and discoloration
Racks | Inspect battery racks for corrosion, cleanliness, proper grounding, and structural integrity, seismic protection
Electrolyte | Inspect electrolyte for containment, leaking, spills, and levels
Ventilation | Inspect ventilation equipment operation, dampers, filters, alarms, and other items that might restrict air movement
Heating | Inspect heating and air conditioning equipment including filters that control ambient room temperature for restricted air movement
Lights | Verify the functionality of lights, strobes, horns, and related alarm notifications
issueTItle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Containers | Inspect containers, covers, and vent caps for cracks and structural damage |  | Basic Visual Inspection Form | Vented Lead-Acid Battery | VLAB | BASIC | visualInspection
Plates | Inspect plates and internal parts when visible | Document excessive positive plate growth, sulfate crystal formation, buckling, warping, scaling, swelling, cracking, hydration rings, excessive sedimentation, mossing, copper contamination, internal post seal cracks, and changes in color.
Cables | Inspect interconnection cables, cell connectors, and other conductors for wear, contamination, corrosion, and discoloration
Racks | Inspect battery racks for corrosion, cleanliness, proper grounding, and structural integrity, seismic protection
Electrolyte | Inspect electrolyte for containment, leaking, spills, and levels
Ventilation | Inspect ventilation equipment operation, dampers, filters, alarms, and other items that might restrict air movement
Heating | Inspect heating and air conditioning equipment including filters that control ambient room temperature for restricted air movement
Lights | Verify the functionality of lights, strobes, horns, and related alarm notifications
issueTItle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Containers | Inspect containers, covers, and vent caps for cracks and structural damage |  | Basic Visual Inspection Form | Valve-Regulated Lead-Acid Battery | VRLB | BASIC | visualInspection
Plates | Inspect plates and internal parts when visible | Document excessive positive plate growth, sulfate crystal formation, buckling, warping, scaling, swelling, cracking, hydration rings, excessive sedimentation, mossing, copper contamination, internal post seal cracks, and changes in color.
Cables | Inspect interconnection cables, cell connectors, and other conductors for wear, contamination, corrosion, and discoloration
Racks | Inspect battery racks for corrosion, cleanliness, proper grounding, and structural integrity, seismic protection
Electrolyte | Inspect electrolyte for containment, leaking, spills, and levels
Ventilation | Inspect ventilation equipment operation, dampers, filters, alarms, and other items that might restrict air movement
Heating | Inspect heating and air conditioning equipment including filters that control ambient room temperature for restricted air movement
Lights | Verify the functionality of lights, strobes, horns, and related alarm notifications
issueTItle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Containers | Inspect containers, covers, and vent caps for cracks and structural damage |  | Basic Visual Inspection Form | Ni-Cad Battery | NICB | BASIC | visualInspection
Plates | Inspect plates and internal parts when visible | Document excessive positive plate growth, sulfate crystal formation, buckling, warping, scaling, swelling, cracking, hydration rings, excessive sedimentation, mossing, copper contamination, internal post seal cracks, and changes in color.
Cables | Inspect interconnection cables, cell connectors, and other conductors for wear, contamination, corrosion, and discoloration
Racks | Inspect battery racks for corrosion, cleanliness, proper grounding, and structural integrity, seismic protection
Electrolyte | Inspect electrolyte for containment, leaking, spills, and levels
Ventilation | Inspect ventilation equipment operation, dampers, filters, alarms, and other items that might restrict air movement
Heating | Inspect heating and air conditioning equipment including filters that control ambient room temperature for restricted air movement
Lights | Verify the functionality of lights, strobes, horns, and related alarm notifications
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Terminal connectors, battery posts, and cable ends shall be checked and be cleaned to remove all corrosion and dirt. |  | NFPA 70B® Enhanced Cleaning Form | Vented Lead-Acid Battery | VLAB | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Terminal connectors, battery posts, and cable ends shall be checked and be cleaned to remove all corrosion and dirt. |  | NFPA 70B® Enhanced Cleaning Form | Valve-Regulated Lead-Acid Battery | VRLB | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Terminal connectors, battery posts, and cable ends shall be checked and be cleaned to remove all corrosion and dirt. |  | NFPA 70B® Enhanced Cleaning Form | Ni-Cad Battery | NICB | 70B-ENHANCED | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Terminal connectors, battery posts, and cable ends shall be checked and be cleaned to remove all corrosion and dirt. |  | NFPA 70B® Standard Cleaning Form | Vented Lead-Acid Battery | VLAB | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Terminal connectors, battery posts, and cable ends shall be checked and be cleaned to remove all corrosion and dirt. |  | NFPA 70B® Standard Cleaning Form | Valve-Regulated Lead-Acid Battery | VRLB | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Terminal connectors, battery posts, and cable ends shall be checked and be cleaned to remove all corrosion and dirt. |  | NFPA 70B® Standard Cleaning Form | Ni-Cad Battery | NICB | 70B-STANDARD | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Terminal connectors, battery posts, and cable ends shall be checked and be cleaned to remove all corrosion and dirt. |  | Basic Cleaning Form | Vented Lead-Acid Battery | VLAB | BASIC | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Terminal connectors, battery posts, and cable ends shall be checked and be cleaned to remove all corrosion and dirt. |  | Basic Cleaning Form | Valve-Regulated Lead-Acid Battery | VRLB | BASIC | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Cleanliness | Terminal connectors, battery posts, and cable ends shall be checked and be cleaned to remove all corrosion and dirt. |  | Basic Cleaning Form | Ni-Cad Battery | NICB | BASIC | cleaning
issueTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Overall float voltage | Overall float voltage | Measured at the battery and verified annually to be in accordance with the battery manufacturer’s instructions. | NFPA 70B® Enhanced Electrical Testing Form | Vented Lead-Acid Battery | VLAB | 70B-ENHANCED | electricalTesting
Measure cell temperature | Measure cell temperature
Specific gravity | Specific gravity | No less than 10% of the units in the string(s).
Ohmic testing | Ohmic testing | Resistance, impedance, or conductance.
Contact resistance | Inspect electrical connection for high resistance
Performance testing | Performance testing
Float current | Float current
Voltage | Individual cell/unit float voltage | Record voltage measurements on individual cells or units to two decimal places.
isseuTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Overall float voltage | Overall float voltage | Measured at the battery and verified annually to be in accordance with the battery manufacturer’s instructions. | NFPA 70B® Enhanced Electrical Testing Form | Valve-Regulated Lead-Acid Battery | VRLB | 70B-ENHANCED | electricalTesting
Measure cell temperature | Measure cell temperature
Specific gravity | Specific gravity | No less than 10% of the units in the string(s).
Ohmic testing | Ohmic testing | Resistance, impedance, or conductance.
Contact resistance | Inspect electrical connection for high resistance
Performance testing | Performance testing
Float current | Float current
Voltage | Individual cell/unit float voltage | Record voltage measurements on individual cells or units to two decimal places.
isseuTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Overall float voltage | Overall float voltage | Measured at the battery and verified annually to be in accordance with the battery manufacturer’s instructions. | NFPA 70B® Enhanced Electrical Testing Form | Ni-Cad Battery | NICB | 70B-ENHANCED | electricalTesting
Measure cell temperature | Measure cell temperature
Specific gravity | Specific gravity | No less than 10% of the units in the string(s).
Ohmic testing | Ohmic testing | Resistance, impedance, or conductance.
Contact resistance | Inspect electrical connection for high resistance
Performance testing | Performance testing
Float current | Float current
Voltage | Individual cell/unit float voltage | Record voltage measurements on individual cells or units to two decimal places.
isseuTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Overall float voltage | Overall float voltage | Measured at the battery and verified annually to be in accordance with the battery manufacturer’s instructions. | NFPA 70B® Standard Electrical Testing Form | Vented Lead-Acid Battery | VLAB | 70B-STANDARD | electricalTesting
Measure cell temperature | Measure cell temperature
Specific gravity | Performance testing
Thermal | Thermal imaging
Float current | Float current
Voltage | Individual cell/unit float voltage | Record voltage measurements on individual cells or units to two decimal places.
isseuTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Overall float voltage | Overall float voltage | Measured at the battery and verified annually to be in accordance with the battery manufacturer’s instructions. | NFPA 70B® Standard Electrical Testing Form | Valve-Regulated Lead-Acid Battery | VRLB | 70B-STANDARD | electricalTesting
Measure cell temperature | Measure cell temperature
Specific gravity | Performance testing
Thermal | Thermal imaging
Float current | Float current
Voltage | Individual cell/unit float voltage | Record voltage measurements on individual cells or units to two decimal places.
isseuTitle | testTitle | tooltip | formTitle | assetClassName | assetClassCode | planName | pmItem
Overall float voltage | Overall float voltage | Measured at the battery and verified annually to be in accordance with the battery manufacturer’s instructions. | NFPA 70B® Standard Electrical Testing Form | Ni-Cad Battery | NICB | 70B-STANDARD | electricalTesting
Measure cell temperature | Measure cell temperature
Specific gravity | Performance testing
Thermal | Thermal imaging
Float current | Float current
Voltage | Individual cell/unit float voltage | Record voltage measurements on individual cells or units to two decimal places.

## 70B Standard Plans
70B CHAPTER / ASSET CLASS GROUP | ASSET CLASS NAME | ASSET CLASS CODE | CONDITION 1 | [5 empty] | CONDITION 2 | [5 empty] | CONDITION 3
|  |  | Infrared Thermography | Visual Inspection | Mechancial Servicing | Cleaning | Lubrication | Fluid Sample Analysis | Infrared Thermography | Visual Inspection | Mechancial Servicing | Cleaning | Lubrication | Fluid Sample Analysis | Infrared Thermography | Visual Inspection | Mechancial Servicing | Cleaning | Lubrication | Fluid Sample Analysis
Ch. 11 - Power & Distribution Transformers | Dry-Type Transformer (<= 600V) | DTTR-LV | 12 | 12 | 60 | 60 | N/A | N/A | 12 | 12 | 36 | 36 | N/A | N/A | 6 | 6 | 12 | 12 | N/A | N/A
| Dry-Type Transformer (> 600V) | DTTR-MV | 12 | 12 | 60 | 60 | N/A | N/A | 12 | 12 | 36 | 36 | N/A | N/A | 6 | 6 | 12 | 12 | N/A | N/A
| Oil-Filled Transformer | OFTR | 12 | 12 | 60 | 60 | N/A | 12 | 12 | 12 | 36 | 36 | N/A | 12 | 6 | 6 | 12 | 12 | N/A | 6
Ch. 12 - Substation & Switchgear | Switchgear (<= 1000V) | SWGR-LV | 12 | 12 | 60 | 60 | 60 | N/A | 12 | 12 | 36 | 36 | 36 | N/A | 6 | 6 | 12 | 12 | 12 | N/A
| Switchgear (> 1000V) | SWGR-MV | 12 | 12 | 60 | 60 | 60 | N/A | 12 | 12 | 36 | 36 | 36 | N/A | 6 | 6 | 12 | 12 | 12 | N/A
| Unitized Substation (USS) (<= 1000V) | USSX-LV | 12 | 12 | 60 | 60 | 60 | N/A | 12 | 12 | 36 | 36 | 36 | N/A | 6 | 6 | 12 | 12 | 12 | N/A
| Unitized Substation (USS) (> 1000V) | USSX-MV | 12 | 12 | 60 | 60 | 60 | N/A | 12 | 12 | 36 | 36 | 36 | N/A | 6 | 6 | 12 | 12 | 12 | N/A
Ch. 13 - Panelboards & Switchboards | Distribution Panelboard | DPNL | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Panelboard | PANL | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Switchboard | SWBD | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
Ch. 14 - Busway | Busway (<= 600V) | BUSW-LV | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 60 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Busway (> 600V) | BUSW-MV | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 60 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
Ch. 15 - Circuit Breakers, Low- and Medium-Voltage | Low-Voltage Molded Case Circuit Breaker (<= 250A) | MCCB-S-LV | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Low-Voltage Molded Case Circuit Breaker (> 250A) | MCCB-L-LV | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Low-Voltage Insulated Case Circuit Breaker | ICCB | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Low-Voltage Power Circuit Breaker | LVCB | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Medium-Voltage Air Magnetic Circuit Breaker | AMCB | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Medium-Voltage Oil Insulated Circuit Breaker | OICB | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Medium-Voltage Vacuum Circuit Breaker | VCCB | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Medim-Votlage Gas Insulated Circuit Breaker | GICB | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
Ch. 16 - Fuses | Fuse (<= 1000V) | FUSE-LV | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Fuse (> 1000V) | FUSE-MV | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
Ch. 17 - Switches | Disconnect Switch (<= 1000V) | DISC-LV | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Disconnect Switch (> 1000V) | DISC-MV | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Fused Disconnect Switch (<= 1000V) | DISC-F-LV | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Fused Disconnect Switch (>1000V) | DISC-F-MV | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Transfer Switch (<= 1000V) | MTSW-LV | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Transfer Switch (> 1000V) | MTSW-MV | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Automatic Transfer Switch (<= 1000V) | ATSW-LV | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Automatic Transfer Switch (> 1000V) | ATSW-MV | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Bolted-Pressure Switch (BPS) | BPSW | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Load-Interruptor Switch | LISW | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| High-Pressure Contact Switch (HPC) | HPSW | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Bypass-Isolation Switch (<= 1000V) | BISW-LV | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Bypass-Isolation Switch (> 1000V) | BISW-MV | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
Ch. 18 - Power Cables & Conductors | Power Cable / Conductor (<= 1000V) | CABL-LV | 12 | 12 | 60 | 60 | 60 | N/A | 12 | 12 | 36 | 36 | 36 | N/A | 6 | 6 | 12 | 12 | 12 | N/A
| Power Cable / Conductor (> 1000V) | CABL-MV | 12 | 12 | 60 | 60 | 60 | N/A | 12 | 12 | 36 | 36 | 36 | N/A | 6 | 6 | 12 | 12 | 12 | N/A
Ch. 19 - Cable Tray | Cable Tray System | CBLT | 12 | 12 | 60 | 60 | 60 | N/A | 12 | 12 | 36 | 36 | 36 | N/A | 6 | 6 | 12 | 12 | 12 | N/A
Ch. 20 - Grounding & Bonding | Grounding | GRND | 12 | 12 | N/A | N/A | N/A | N/A | 12 | 12 | N/A | N/A | N/A | N/A | 6 | 6 | N/A | N/A | N/A | N/A
| Bonding | BNDG | 12 | 12 | N/A | N/A | N/A | N/A | 12 | 12 | N/A | N/A | N/A | N/A | 6 | 6 | N/A | N/A | N/A | N/A
Ch. 21 - Ground Fault Protection System | Low-Voltage Integral Ground Fault Protection System | GFPS-I-LV | 12 | 12 | 60 | 60 | N/A | N/A | 12 | 12 | 36 | 36 | N/A | N/A | 6 | 6 | 36 | 36 | N/A | N/A
| Low-Voltage External Ground Fault Protection System | GFPS-E-LV | 12 | 12 | 60 | 60 | N/A | N/A | 12 | 12 | 36 | 36 | N/A | N/A | 6 | 6 | 36 | 36 | N/A | N/A
| Medium-Voltage Integral Ground Fault Protection System | GFPS-I-MV | 12 | 12 | 60 | 60 | N/A | N/A | 12 | 12 | 36 | 36 | N/A | N/A | 6 | 6 | 36 | 36 | N/A | N/A
| Medium-Voltage External Ground Fault Protection System | GFPS-E-MV | 12 | 12 | 60 | 60 | N/A | N/A | 12 | 12 | 36 | 36 | N/A | N/A | 6 | 6 | 36 | 36 | N/A | N/A
Ch. 25 - Uninterruptible Power Supplies (UPS) | Static UPS System | UPSS | 12 | 6 | 12 | 12 | N/A | N/A | 12 | 3 | 6 | 6 | N/A | N/A | 6 | 1 | 3 | 3 | N/A | N/A
| Rotary UPS System | UPSR | 12 | 6 | 12 | 12 | N/A | N/A | 12 | 3 | 6 | 6 | N/A | N/A | 6 | 1 | 3 | 3 | N/A | N/A
| Hybrid UPS System | UPSH | 12 | 6 | 12 | 12 | N/A | N/A | 12 | 3 | 6 | 6 | N/A | N/A | 6 | 1 | 3 | 3 | N/A | N/A
Ch. 27 - Rotating Equipment | Low-Voltage Machine (<= 200hp) | LVMT-S | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Low-Voltage Machine (>200hp) | LVMT-L | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Low-Voltage Machine (dc) | LVMT-DC | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Medium-Voltage Induction Machine | MVIN | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Medium-Voltage Synchronous Machine | MVSC | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
Ch. 28 - Motor Control Equipment | Motor Control Equipment (<= 1000V) | MCEQ-LV | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
| Motor Control Equipment (> 1000V) | MCEQ-MV | 12 | 60 | 60 | 60 | 60 | N/A | 12 | 36 | 36 | 36 | 36 | N/A | 6 | 12 | 12 | 12 | 12 | N/A
Ch. 30 - Photovoltaic Systems | Solar Photovoltaic System | SOLR | 12 | 60 | N/A | N/A | N/A | N/A | 12 | 36 | N/A | N/A | N/A | N/A | 6 | 12 | N/A | N/A | N/A | N/A
Ch. 31 - Wind Power Electric Systems / Equipment | Wind Power System | WIND | 12 | 60 | 60 | 60 | N/A | N/A | 12 | 36 | 36 | 36 | N/A | N/A | 6 | 12 | 12 | 12 | N/A | N/A
Ch. 32 - Battery Energy Storage Systems | Battery Energy Storage System (ESS) | BESS | 12 | 60 | N/A | 60 | N/A | N/A | 12 | 36 | N/A | 36 | N/A | N/A | 6 | 12 | N/A | 12 | N/A | N/A
Ch. 33 - Electric Vehicle Charging Stations | Electrical Vehicle Charging Station | EVCS | 12 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | N/A | N/A | N/A
Ch. 35 - Protective Relays | Electromechanical Relay | EMRE | 12 | 36 | 36 | 36 | N/A | N/A | 12 | 24 | 24 | 24 | N/A | N/A | 6 | 12 | 12 | 12 | N/A | N/A
| Solid-State Relay | SSRE | 12 | 60 | 60 | 60 | N/A | N/A | 12 | 36 | 36 | 36 | N/A | N/A | 6 | 12 | 12 | 12 | N/A | N/A
| Microprocessor Relay | MPRE | 12 | 60 | 60 | 60 | N/A | N/A | 12 | 36 | 36 | 36 | N/A | N/A | 6 | 12 | 12 | 12 | N/A | N/A
Ch. 36 - Batteries | Vented Lead-Acid Battery | VLAB | 12 | 60 | N/A | 60 | N/A | N/A | 12 | 36 | N/A | 36 | N/A | N/A | 6 | 12 | N/A | 12 | N/A | N/A
| Valve-Regulated Lead-Acid Battery | VRLB | 12 | 60 | N/A | 60 | N/A | N/A | 12 | 36 | N/A | 36 | N/A | N/A | 6 | 12 | N/A | 12 | N/A | N/A
| Ni-Cad Battery | NICB | 12 | 60 | N/A | 60 | N/A | N/A | 12 | 36 | N/A | 36 | N/A | N/A | 6 | 12 | N/A | 12 | N/A | N/A
Ch. 37 - Instrument Transformers | Current Transformer | CITR | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 6 |  |  |  |  | N/A
| Potential Transformer | PITR | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 6 |  |  |  |  | N/A
EEE - Meters | Ammeter | AMME | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 6 |  |  |  |  | N/A
| Votmeter | VVME | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 6 |  |  |  |  | N/A
| Watt-Hour Meter | WHME | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 6 |  |  |  |  | N/A
| Line Isolation Monitor | LIMI | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 6 |  |  |  |  | N/A
| Multimeter | MMME | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 6 |  |  |  |  | N/A
EEE - Unclassified | Surge Capacitor | SCAP | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 6 |  |  |  |  | N/A
| Power Factor Correction Capacitor | PCAP | 12 | 60 | 60 | 60 | N/A | N/A | 12 | 36 | 36 | 36 | N/A | N/A | 6 | 12 | 12 | 12 | N/A | N/A
| Lightning Arrester | LAAR | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 6 |  |  |  |  | N/A
| Recitifier | RCTF | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 6 |  |  |  |  | N/A
| Inverter | INVR | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 6 |  |  |  |  | N/A
| Recloser | RCLS | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 6 |  |  |  |  | N/A
| Generator | GENR | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 7 |  |  |  |  | N/A
| Contactor | CTCR | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 8 |  |  |  |  | N/A
| Low-Voltage Surge Protector | SPRT-LV | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 8 |  |  |  |  | N/A
| Ground Resistor | REGR | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 8 |  |  |  |  | N/A
| Reactor | REAC | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 6 |  |  |  |  | N/A
For modeling use | Power Distribution Unit | PDUX | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 6 |  |  |  |  | N/A
| Fuse Box | FSBX | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 6 |  |  |  |  | N/A
| Junction Box | JCBX | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 6 |  |  |  |  | N/A
| Combiner Box | CBBX | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 6 |  |  |  |  | N/A
For general modeling use | General Enclosure | ENCL | 12 |  |  |  |  | N/A | 12 |  |  |  |  | N/A | 6 |  |  |  |  | N/A
| General Endpoint | ENDX | N/A |  |  |  |  | N/A | N/A |  |  |  |  | N/A | N/A |  |  |  |  | N/A
| Other | Other | N/A |  |  |  |  | N/A | N/A |  |  |  |  | N/A | N/A |  |  |  |  | N/A

## 70B Enhanced Plans
70B CHAPTER / ASSET CLASS GROUP | ASSET CLASS NAME | ASSET CLASS CODE | CONDITION 1 | [8 empty] | CONDITION 2 | [8 empty] | CONDITION 3
|  |  | Infrared Thermography | Visual Inspection | Mechancial Servicing | Cleaning | Lubrication | Electrical Testing | Special | Fluid Sample Analysis | Battery Performance Testing | Infrared Thermography | Visual Inspection | Mechancial Servicing | Cleaning | Lubrication | Electrical Testing | Special | Fluid Sample Analysis | Battery Performance Testing | Infrared Thermography | Visual Inspection | Mechancial Servicing | Cleaning | Lubrication | Electrical Testing | Special | Fluid Sample Analysis | Battery Performance Testing
Ch. 11 - Power & Distribution Transformers | Dry-Type Transformer (<= 600V) | DTTR-LV | 12 | 12 | 60 | 60 | N/A | 60 | N/A | N/A | N/A | 12 | 12 | 36 | 36 | N/A | 36 | N/A | N/A | N/A | 6 | 6 | 12 | 12 | N/A | 12 | N/A | N/A | N/A
| Dry-Type Transformer (> 600V) | DTTR-MV | 12 | 12 | 60 | 60 | N/A | 60 | N/A | N/A | N/A | 12 | 12 | 36 | 36 | N/A | 36 | N/A | N/A | N/A | 6 | 6 | 12 | 12 | N/A | 12 | N/A | N/A | N/A
| Oil-Filled Transformer | OFTR | 12 | 12 | 60 | 60 | N/A | 60 | N/A | 12 | N/A | 12 | 12 | 36 | 36 | N/A | 36 | N/A | 12 | N/A | 6 | 6 | 12 | 12 | N/A | 12 | N/A | 6 | N/A
Ch. 12 - Substation & Switchgear | Switchgear (<= 1000V) | SWGR-LV | 12 | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | 12 | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | 6 | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A
| Switchgear (> 1000V) | SWGR-MV | 12 | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | 12 | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | 6 | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A
| Unitized Substation (USS) (<= 1000V) | USSX-LV | 12 | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | 12 | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | 6 | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A
| Unitized Substation (USS) (> 1000V) | USSX-MV | 12 | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | 12 | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | 6 | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A
Ch. 13 - Panelboards & Switchboards | Distribution Panelboard | DPNL | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Panelboard | PANL | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Switchboard | SWBD | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
Ch. 14 - Busway | Busway (<= 600V) | BUSW-LV | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 60 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Busway (> 600V) | BUSW-MV | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 60 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
Ch. 15 - Circuit Breakers, Low- and Medium-Voltage | Low-Voltage Molded Case Circuit Breaker (<= 250A) | MCCB-S-LV | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Low-Voltage Molded Case Circuit Breaker (> 250A) | MCCB-L-LV | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Low-Voltage Insulated Case Circuit Breaker | ICCB | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Low-Voltage Power Circuit Breaker | LVCB | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Medium-Voltage Air Magnetic Circuit Breaker | AMCB | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Medium-Voltage Oil Insulated Circuit Breaker | OICB | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Medium-Voltage Vacuum Circuit Breaker | VCCB | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Medim-Votlage Gas Insulated Circuit Breaker | GICB | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
Ch. 16 - Fuses | Fuse (<= 1000V) | FUSE-LV | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Fuse (> 1000V) | FUSE-MV | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
Ch. 17 - Switches | Disconnect Switch (<= 1000V) | DISC-LV | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Disconnect Switch (> 1000V) | DISC-MV | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Fused Disconnect Switch (<= 1000V) | DISC-F-LV | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Fused Disconnect Switch (>1000V) | DISC-F-MV | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Transfer Switch (<= 1000V) | MTSW-LV | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Transfer Switch (> 1000V) | MTSW-MV | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Automatic Transfer Switch (<= 1000V) | ATSW-LV | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Automatic Transfer Switch (> 1000V) | ATSW-MV | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Bolted-Pressure Switch (BPS) | BPSW | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Load-Interruptor Switch | LISW | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| High-Pressure Contact Switch (HPC) | HPSW | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Bypass-Isolation Switch (<= 1000V) | BISW-LV | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Bypass-Isolation Switch (> 1000V) | BISW-MV | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
Ch. 18 - Power Cables & Conductors | Power Cable / Conductor (<= 1000V) | CABL-LV | 12 | 12 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 12 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 6 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Power Cable / Conductor (> 1000V) | CABL-MV | 12 | 12 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 12 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 6 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
Ch. 19 - Cable Tray | Cable Tray System | CBLT | 12 | 12 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 12 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 6 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
Ch. 20 - Grounding & Bonding | Grounding | GRND | 12 | 12 | N/A | N/A | N/A | 60 | N/A | N/A | N/A | 12 | 12 | N/A | N/A | N/A | 36 | N/A | N/A | N/A | 6 | 6 | N/A | N/A | N/A | 36 | N/A | N/A | N/A
| Bonding | BNDG | 12 | 12 | N/A | N/A | N/A | 60 | N/A | N/A | N/A | 12 | 12 | N/A | N/A | N/A | 36 | N/A | N/A | N/A | 6 | 6 | N/A | N/A | N/A | 36 | N/A | N/A | N/A
Ch. 21 - Ground Fault Protection System | Low-Voltage Integral Ground Fault Protection System | GFPS-I-LV | 12 | 12 | 60 | 60 | N/A | N/A | N/A | N/A | N/A | 12 | 12 | 36 | 36 | N/A | N/A | N/A | N/A | N/A | 6 | 6 | 36 | 36 | N/A | N/A | N/A | N/A | N/A
| Low-Voltage External Ground Fault Protection System | GFPS-E-LV | 12 | 12 | 60 | 60 | N/A | N/A | N/A | N/A | N/A | 12 | 12 | 36 | 36 | N/A | N/A | N/A | N/A | N/A | 6 | 6 | 36 | 36 | N/A | N/A | N/A | N/A | N/A
| Medium-Voltage Integral Ground Fault Protection System | GFPS-I-MV | 12 | 12 | 60 | 60 | N/A | N/A | N/A | N/A | N/A | 12 | 12 | 36 | 36 | N/A | N/A | N/A | N/A | N/A | 6 | 6 | 36 | 36 | N/A | N/A | N/A | N/A | N/A
| Medium-Voltage External Groudn Fault Protection System | GFPS-E-MV | 12 | 12 | 60 | 60 | N/A | N/A | N/A | N/A | N/A | 12 | 12 | 36 | 36 | N/A | N/A | N/A | N/A | N/A | 6 | 6 | 36 | 36 | N/A | N/A | N/A | N/A | N/A
Ch. 25 - Uninterruptible Power Supplies (UPS) | Static UPS System | UPSS | 12 | 6 | 12 | 12 | N/A | 12 | 24 | N/A | N/A | 12 | 3 | 6 | 6 | N/A | 6 | 24 | N/A | N/A | 6 | 1 | 3 | 3 | N/A | 3 | 24 | N/A | N/A
| Rotary UPS System | UPSR | 12 | 6 | 12 | 12 | N/A | 12 | 24 | N/A | N/A | 12 | 3 | 6 | 6 | N/A | 6 | 24 | N/A | N/A | 6 | 1 | 3 | 3 | N/A | 3 | 24 | N/A | N/A
| Hybrid UPS System | UPSH | 12 | 6 | 12 | 12 | N/A | 12 | 24 | N/A | N/A | 12 | 3 | 6 | 6 | N/A | 6 | 24 | N/A | N/A | 6 | 1 | 3 | 3 | N/A | 3 | 24 | N/A | N/A
Ch. 27 - Rotating Equipment | Low-Voltage Machine (<= 200hp) | LVMT-S | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Low-Voltage Machine (>200hp) | LVMT-L | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Low-Voltage Machine (dc) | LVMT-DC | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Medium-Voltage Induction Machine | MVIN | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Medium-Voltage Synchronous Machine | MVSC | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
Ch. 28 - Motor Control Equipment | Motor Control Equipment (<= 1000V) | MCEQ-LV | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
| Motor Control Equipment (> 1000V) | MCEQ-MV | 12 | 60 | 60 | 60 | 60 | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | 36 | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | 12 | 12 | N/A | N/A | N/A
Ch. 30 - Photovoltaic Systems | Solar Photovoltaic System | SOLR | 12 | 60 | N/A | N/A | N/A | 60 | N/A | N/A | N/A | 12 | 36 | N/A | N/A | N/A | 36 | N/A | N/A | N/A | 6 | 12 | N/A | N/A | N/A | 12 | N/A | N/A | N/A
Ch. 31 - Wind Power Electric Systems / Equipment | Wind Power System | WIND | 12 | 60 | 60 | 60 | N/A | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | N/A | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | N/A | 12 | N/A | N/A | N/A
Ch. 32 - Battery Energy Storage Systems | Battery Energy Storage System (ESS) | BESS | 12 | 60 | N/A | 60 | N/A | 60 | N/A | N/A | 36 | 12 | 36 | N/A | 36 | N/A | 36 | N/A | N/A | 36 | 6 | 12 | N/A | 12 | N/A | 12 | N/A | N/A | 12
Ch. 33 - Electric Vehicle Charging Stations | Electrical Vehicle Charging Station | EVCS | 12 | 60 | 60 | N/A | N/A | 60 | N/A | N/A | N/A | 12 | 36 | 36 | N/A | N/A | 36 | N/A | N/A | N/A | 6 | 12 | 12 | N/A | N/A | 12 | N/A | N/A | N/A
Ch. 35 - Protective Relays | Electromechanical Relay | EMRE | 12 | 36 | 36 | 36 | N/A | 36 | N/A | N/A | N/A | 12 | 24 | 24 | 24 | N/A | 24 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | N/A | 12 | N/A | N/A | N/A
| Solid-State Relay | SSRE | 12 | 60 | 60 | 60 | N/A | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | N/A | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | N/A | 12 | N/A | N/A | N/A
| Microprocessor Relay | MPRE | 12 | 60 | 60 | 60 | N/A | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | N/A | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | N/A | 12 | N/A | N/A | N/A
Ch. 36 - Batteries | Vented Lead-Acid Battery | VLAB | 12 | 60 | N/A | 60 | N/A | 60 | N/A | N/A | 60 | 12 | 36 | N/A | 36 | N/A | 36 | N/A | N/A | 60 | 6 | 12 | N/A | 12 | N/A | 12 | N/A | N/A | 12
| Valve-Regulated Lead-Acid Battery | VRLB | 12 | 60 | N/A | 60 | N/A | 60 | N/A | N/A | 24 | 12 | 36 | N/A | 36 | N/A | 36 | N/A | N/A | 24 | 6 | 12 | N/A | 12 | N/A | 12 | N/A | N/A | 12
| Ni-Cad Battery | NICB | 12 | 60 | N/A | 60 | N/A | 60 | N/A | N/A | 60 | 12 | 36 | N/A | 36 | N/A | 36 | N/A | N/A | 60 | 6 | 12 | N/A | 12 | N/A | 12 | N/A | N/A | 12
Ch. 37 - Instrument Transformers | Current Transformer | CITR | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
| Potential Transformer | PITR | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
EEE - Meters | Ammeter | AAME | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
| Votmeter | VVME | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
| Watt-Hour Meter | WHME | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
| Line Isolation Monitor | LIMI | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
| Multimeter | MMME | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
EEE - Unclassified | Surge Capacitor | SCAP | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
| Power Factor Correction Capacitor | PCAP | 12 | 60 | 60 | 60 | N/A | 60 | N/A | N/A | N/A | 12 | 36 | 36 | 36 | N/A | 36 | N/A | N/A | N/A | 6 | 12 | 12 | 12 | N/A | 12 | N/A | N/A | N/A
| Lightning Arrester | LAAR | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
| Recitifier | RCTF | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
| Inverter | INVR | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
| Recloser | RCLS | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
| Generator | GENR | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
| Contactor | CTCR | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
| Low-Voltage Surge Protector | SPRT-LV | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
| Ground Resistor | REGR | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
| Reactor | REAC | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
For modeling use | Power Distribution Unit | PDUX | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
| Fuse Box | FSBX | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
| Junction Box | JCBX | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
| Combiner Box | CBBX | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
For general modeling use | General Enclosure | ENCL | 12 | [5 empty] | N/A | N/A | N/A | 12 | [5 empty] | N/A | N/A | N/A | 6 | [5 empty] | N/A | N/A | N/A
| General Endpoint | ENDX | N/A | [5 empty] | N/A | N/A | N/A | N/A | [5 empty] | N/A | N/A | N/A | N/A | [5 empty] | N/A | N/A | N/A
| Other | Other | N/A | [5 empty] | N/A | N/A | N/A | N/A | [5 empty] | N/A | N/A | N/A | N/A | [5 empty] | N/A | N/A | N/A